## Setup
Enter Stakeholder Committee Name in cell A2:
Interconnection Process Subcommittee
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Capacity Interconnection Rights (CIR) Transfer Efficiency

## 1. Interest Identification
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
Interest Identification
Instructions: List interests of all parties on this page.
1 | Allow for an efficient and timely process to minimize diverting resources away from cluster interconnection request studies
2 | Ensure no discriminatory impacts to other interconnection processes
3 | Ensure system capability is being utilized and granted equitably
4 | Establish a clear queue priority among Replacement Generation requests
5 | Minimize impacts to existing rules and requirements associated with Deactivation resources/process
6 | Maintain site control requirements for Replacement resource
7 | Ensure PJM system reliability and scope of reliability studies is not degraded
8 | Ensure Affected System coordination is maintained for Affected System reliability
9 | Clearly address what to do with the existing Replacement Gen requests
10 | Transparent and nondiscriminatory
11 | Open to all current and future Interconnection Customers
12 | Replace all, or a portion of, an Existing Generating Facility with a newer and more efficient Generating Facility
13 | Apply “First Ready, First Served” principals to Replacement Generation requests
14 | Minimize study requirements for Replacement Generation
15 | Minimize financial security requirements for Replacement Generation requests.
16 | Allow interconnection requests with the same POI to be segmented by time
17 | Allow interconnection requests with the same POI to be segmented by developer
18 | Retain the ability for interconnection requests with the same POI to be segmented by technology
19 | Allow interconnection requests with the same POI to mix and match segmentation by time, developer, and technology
20 | Ensure no discriminatory impacts to projects currently in the queue, specifically in regard to queue priority and network upgrade cost allocations
21 | Allow exisiting generators to replace retiring resources with any and all fuel sources and technologies. For example thermal resources to battery storage.
22 | No unnecessary delays in bringing new resources online to ensure resource adequacy
23

## 2. Options Matrix- Design Comp.
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E
* | Implementation
1 | Eligible deactivating resources |  | All generation resources provided that the resource has CIRs (i.e. Capacity Generation Resources) & the resource has submitted an official Deactivation Notice to PJM (PJM comment) | Status Quo (These are Solution Options, so a Status Quo option is not needed. Status Quo can be used as an option in the Package Matrix tab when we get to package building)
2 | Eligible replacement resources |  | All generation resources provided that the resource has requested CIRs with their New Serivce Request application (i.e. requested to be a Capacity Generation Resource) | All generation resources provided that the resource has requested CIRs with their Generator Replacement application (i.e. requested to be a Capacity Generation Resource)
3 | Criteria for determining a transfer under this process is permissible |  | All generation resources provided that the resources have CIRs (i.e. Capacity Generation Resources). The same CIR holder for both the deactivation resource and the replacement resource. A deactivation notice submitted to PJM. Submission of a new service request application and notice to intent to transfer CIRs form prior to CIRs expiring. | All generation resources, including energy storage, provided that the resources have CIRs (i.e. Capacity Generation Resources). The same CIR holder for both the deactivation resource and the replacement resource. A deactivation notice submitted to PJM or notification of anticipated date range of retirement submitted to PJM. Expedited evaluation of generator retire-replacement ("Generator Retirement Process") via a stand alone process outside of PJM's New Service Request Process.
4 | New/Modified Defintions (i.e. Material Modifcation) |  | PJM Tariff Definitions, Attachment P, Appendix 2, section 3.4.l. (Material Modification) PJM Comment: in new Cycle Process, reference OATT Part VIII, Subpart A, section 400 Definitions | Material Modification shall mean (1) modification to an Interconnection Request in the queue that has a material adverse impact on the cost or timing of any other Interconnection Request with a later Queue priority date unless willing to be mitigated by the modifying facility; or (2) planned modification to an Existing Generating Facility that is undergoing evaluation for a Generating Facility Modification or Generating Facility Replacement, and has a material adverse impact on the Transmission System with respect to: i) steady-state thermal or voltage limits, ii) dynamic system stability and response, or iii) short-circuit capability limit; compared to the impacts of the Existing Generating Facility prior to the modification or replacement. The addition of a generating facility, for example, an energy storage resource addition, to a pending interconnection request or planned modification to an Existing Generating Facility that is undergoing evaluation for a Generating Facility Modification or Generating Facility Replacement, will not automatically be deemed a material modification.
5 | OASIS Posting-Generating Facility Replacement Request(s) PJM Comment: public posting of Replacement Requests may not be on PJM OASIS…..suggest revising to more generic Design Component of "Public Posting of Replacement Gen Requests". |  | Such notification of transfer of CIRs shall be posted on Transmission Provider’s public website. PJM Comment: the Status Quo for posting is: "CIR Transfers to Replacement Resources are assigned a PJM Project Identifier within the PJM New Service Request process and posted to the PJM New Service Request webpage." | Additonal language to existing defintion/requirements pertaining to Generating Facility Replacement Requests; "for a Generating Facility Replacement, the planned date of cessation of operation for the Existing Generating Facility, notification of anticipated date range of retirement submitted to PJM or actual date if the Existing Generating Facility already has ceased commercial operations, the expected Commercial Operation Date of the replacement facility and requested Interconnection Service."
6 | Must connect at the same electrical POI as the existing facility PJM Comment: suggest revising this Design Component to "POI Requirements of Replacement Resource". As presently stated, it sounds like a specific Requirement/Solution. |  | Replacement generation resource is not required to be located at the same Point of Interconnection (POI) as the Deactivation generation resource | Any Replacement Generating Facility must connect to the Transmission System at the same or electrically equivalent Point of Interconnection (i.e. same voltage level at the interconnecting substation) as the Existing Generating Facility.
7 | Interconnection Request up to the MW amount of the existing facility PJM Comment: suggest revising this Design Component to "MW Requirements of Replacement Resource". As presently stated, it sounds like a specific Requirement/Solution. |  | The holder of the CIRs will retain only such rights that are commensurate with the size in megawatts of the replacement generation, not to exceed the amount of the holder’s Capacity Interconnection Rights associated with the facility upon Deactivation or removal of Capacity Resource status. The replacement gen request has no upper limit on the CIRs they are requesting. | Status Quo (These are Solution Options, so a Status Quo option is not needed. Status Quo can be used as an option in the Package Matrix tab when we get to package building)
8 | Initiation of CIR Transfer Process |  | The same CIR owner holder for deactivation resource and replacement resource. Requirement of a deactivation notice to PJM. Submission of new service request application and notice to intent to transfer CIRs form prior to CIRs expiring. Application must be submitted before CIRs expire, which is 1 year after the Actual Deactivation Date. (PJM suggested edits) | The request for Generating Facility Replacement must be submitted at least one (1) year prior to the date that the Existing Generating Facility will cease operation unless the Existing Generating Facility is in suspension or in Forced Outage, and must include the planned date of cessation of operation for the Existing Generating Facility or anticipated date range of planned cessation of opeation and the expected Commercial Operation Date for the Replacement Generating Facility. An Interconnection Customer (IC) shall submit to PJM a Generating Facility Replacement request by providing an executed study agreement and the deposit. |  |  |  |  | Low
9 | Commercial Operation date of replacement generation |  | As determined in the GIA. | No more than three (3) years from the date of execution of the GIA or four (4) years from the date a unit is determined to be in forced outage. If the requested period of time between the cessation of operation of the Existing Generating Facility and expected Commercial Operation Date of the Replacement Generating Facility is more than three (3) years from the execution of the GIA, the request shall be treated as Interconnection request for a new Generating Facility. |  |  |  |  | Low - Medium
10 | Serial Processing of the Generator Replacement Request PJM Comment: suggest revising this Design Component to "Queue priority among Replacement Resource requests". As presently stated, it sounds like a specific Requirement/Solution. |  | The Replacement generation resource, along with the CIR Transfer, is evaluated and processed as part of the PJM New Services Request Process. | The Replacement generation resource, along with the CIR Transfer, is evaluated and processed in the order in which they are submitted. |  |  |  |  | Low - High
11 | PJM evaluation / Screening: (Replacement Impact Study (RIS) & Replacement Realiability Study (RAS)- (Completed within 180 Days),Replacement Facilities Study (if necessary; Completed within 90 Days of RIS & RAS) PJM Comment: this Design Component sounds like specific details of a Solution. Suggest revising to "Screening criteria, Study Phases, and scope of each Study Phase". |  | Transfers of CIRs will be is evaluated through System Impact Studies (Phases 1-3 of Cycle Process) performed by PJM (including load flow, short circuit and stability). (PJM suggested edits.) | The evaluation will consist of two studies: i) a Replacement Impact Study and ii) a Reliability Assessment Study. PJM shall use Reasonable Efforts to complete the Replacement Impact Study and Reliability Assessment Study and share results with the IC within one hundred eighty (180) Calendar Days of the request. |  |  |  |  | Medium
12 | Replacement Facilities Study |  | Transfers of CIRs will be evaluated through System Impact Studies performed by PJM (including load flow, short circuit and stability). | If PJM determines such a study is necessary, upon IC’s notice to proceed to PJM after completion of the RIS and the RAS. This Interconnection Facilities Study will identify estimates for cost and the time required to construct the Interconnection Facilities. PJM shall use Reasonable Efforts to complete this portion of the Interconnection Facilities Study within ninety (90) Calendar Days.
13 | Criteria for Generator Replacement Requests that are found to have adverse impacts to transmission system and/or request interconnection service in excess of the existing generator facility that is being replaced. |  | The Replacement generation resource is part of a Cycle within the PJM New Services Request Process and cost responsibility may be shared with other New Service Requests in the same Cycle, if impacts are found | If the removal of the existing generator would lead to material reliability issue on the grid, then PJM will address such issues as a regional reliability upgrade, and the Interconnection Request will be processed under the proposed Generator Replacement Rules. If a material impact is identified that is caused by the proposed new Generating Facility, the IC will be notified and provided an opportunity to modify its proposed facility to remove the adverse impact or to sponsor upgrades required to remove the adverse impact.
14 | Study Agreement with deposit for all requests PJM Comment: suggest revising this Design Component to "Application and Deposit Requirements". As presently stated, it sounds like a specific Requirement/Solution. |  | Applicant must submit any claim from the deactivating generating units with their application, and it must be received by the Application Deadline. CIR claims must be submitted using the CIR Transfer template available on the PJM website. Deposit based on PJM's new process. | Status Quo (These are Solution Options, so a Status Quo option is not needed. Status Quo can be used as an option in the Package Matrix tab when we get to package building)
15 | Customer decision point upon posting of study results to decide to proceed PJM Comment: this Design Component sounds like specific details of a Solution. Suggest revising to "Decision Points during Study Process". |  | There will be are decision points 1, 2, and 3 after Phases 1,2,3 of the Cycle Process. (PJM suggested edits.) | IC requesting Generating Facility Replacement shall inform PJM within thirty (30) Calendar Days after having received results of the RIS and RAS of its election to proceed and PJM will initiate a Facilities Study or tender a draft GIA. Failure by the IC to provide an election to proceed within thirty (30) Calendar Days will result in withdrawal of the Interconnection Request
16 | GIA will be issued per current tariff requirements PJM Comment: this Design Component sounds like specific details of a Solution. Suggest revising to "GIA Requirements". |  | GIA issued for Replacement resource as part of the New Services Request Process, per the OATT sections covering the New Services Request Process | PJM shall tender a draft GIA to the IC thirty (30) Calendar Days after the IC communicates its election to proceed with Generator Replacement if a Facilities Study is not required or within thirty (30) Calendar Days after final Facility Study reports are provided to the IC. The draft GIA shall include appendices describing the timing of Generating Facility Replacement and a condition that the GIA cannot be assigned and the Replacement Generating Facility cannot be transferred to any other Party, including an affiliate of the IC, until such date as the Replacement Generating Facility achieves commercial operation.
17 | Site Control Requirements |  | Replacement resource site control requirements per OATT Part VIII, Subpart A, section 402, under the Cycle Process
18 | Application Submission Windows/Periods |  | Cycle Process - each Cycle has an Application Phase to accept Applications. See PJM Manual 14H, Section 2 "Application Phase".
19 | Queue priority between Replacement Resource requests and other Interconnection Requests in the Cycle Process |  | Replacement Resource requests are processed in the Cycle Process with other Interconnection requests
20 | Scope of Reliability studies to be performed |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII). Main reliability studies include powerflow at various load levels, short circuit, stability, Affected System studies, TO analysis per TO Local Planning criteria.
21 | Cost responsibility/allocation rules for any identified required network upgrades for Replacement Resource |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII) and network upgrades are cost allocated among all projects in a given Cycle if they meet PJM cost allocation thresholds as outlined in M14H, Att. B.
22 | Processing of existing Replacement Generation requests |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII)
23 | Type of interconnection service for the Replacement Generating Facility (Energy Resource Interconnection Service (ERIS) vs Network Resource Interconnection Service (NRIS)) |  |  | Interconnection Customer may request only ER Interconnection Service (ERIS) for the Replacement Generating Facility if the Existing Generating Facility has ERIS. Interconnection Customer may request either ERIS or NR Interconnection Service (NRIS) for the Replacement Generating Facility if the Existing Generating Facility has NRIS.
24 | Customer Modification of Replacement Generation Request |  |  | Replacement Generating Facility can be modified any time before the evaluation process is complete.
25 | Clear definition of "material adverse impact(s)"
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attibute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1 | Eligible deactivating resources |  | All generation resources provided that the resource has CIRs (i.e. Capacity Generation Resources) & the resource has submitted an official Deactivation Notice to PJM (PJM comment)
2 | Eligible replacement resources |  | All generation resources provided that the resource has requested CIRs with their New Serivce Request application (i.e. requested to be a Capacity Generation Resource)
3 | Criteria for determining a transfer under this process is permissible |  | All generation resources provided that the resources have CIRs (i.e. Capacity Generation Resources). The same CIR holder for both the deactivation resource and the replacement resource. A deactivation notice submitted to PJM. Submission of a new service request application and notice to intent to transfer CIRs form prior to CIRs expiring.
4 | New/Modified Defintions (i.e. Material Modifcation) |  | PJM Tariff Definitions, Attachment P, Appendix 2, section 3.4.l. (Material Modification) PJM Comment: in new Cycle Process, reference OATT Part VIII, Subpart A, section 400 Definitions
5 | OASIS Posting-Generating Facility Replacement Request(s) PJM Comment: public posting of Replacement Requests may not be on PJM OASIS…..suggest revising to more generic Design Component of "Public Posting of Replacement Gen Requests". |  | Such notification of transfer of CIRs shall be posted on Transmission Provider’s public website. PJM Comment: the Status Quo for posting is: "CIR Transfers to Replacement Resources are assigned a PJM Project Identifier within the PJM New Service Request process and posted to the PJM New Service Request webpage."
6 | Must connect at the same electrical POI as the existing facility PJM Comment: suggest revising this Design Component to "POI Requirements of Replacement Resource". As presently stated, it sounds like a specific Requirement/Solution. |  | Replacement generation resource is not required to be located at the same Point of Interconnection (POI) as the Deactivation generation resource
7 | Interconnection Request up to the MW amount of the existing facility PJM Comment: suggest revising this Design Component to "MW Requirements of Replacement Resource". As presently stated, it sounds like a specific Requirement/Solution. |  | The holder of the CIRs will retain only such rights that are commensurate with the size in megawatts of the replacement generation, not to exceed the amount of the holder’s Capacity Interconnection Rights associated with the facility upon Deactivation or removal of Capacity Resource status. The replacement gen request has no upper limit on the CIRs they are requesting.
8 | Initiation of CIR Transfer Process |  | The same CIR owner holder for deactivation resource and replacement resource. Requirement of a deactivation notice to PJM. Submission of new service request application and notice to intent to transfer CIRs form prior to CIRs expiring. Application must be submitted before CIRs expire, which is 1 year after the Actual Deactivation Date. (PJM suggested edits)
9 | Commercial Operation date of replacement generation |  | As determined in the GIA.
10 | Serial Processing of the Generator Replacement Request PJM Comment: suggest revising this Design Component to "Queue priority among Replacement Resource requests". As presently stated, it sounds like a specific Requirement/Solution. |  | The Replacement generation resource, along with the CIR Transfer, is evaluated and processed as part of the PJM New Services Request Process.
11 | PJM evaluation / Screening: (Replacement Impact Study (RIS) & Replacement Realiability Study (RAS)- (Completed within 180 Days),Replacement Facilities Study (if necessary; Completed within 90 Days of RIS & RAS) PJM Comment: this Design Component sounds like specific details of a Solution. Suggest revising to "Screening criteria, Study Phases, and scope of each Study Phase". |  | Transfers of CIRs will be is evaluated through System Impact Studies (Phases 1-3 of Cycle Process) performed by PJM (including load flow, short circuit and stability). (PJM suggested edits.)
12 | Criteria for Generator Replacement Requests that are found to have adverse impacts to transmission system and/or request interconnection service in excess of the existing generator facility that is being replaced. |  | The Replacement generation resource is part of a Cycle within the PJM New Services Request Process and cost responsibility may be shared with other New Service Requests in the same Cycle, if impacts are found
13 | Study Agreement with deposit for all requests PJM Comment: suggest revising this Design Component to "Application and Deposit Requirements". As presently stated, it sounds like a specific Requirement/Solution. |  | Applicant must submit any claim from the deactivating generating units with their application, and it must be received by the Application Deadline. CIR claims must be submitted using the CIR Transfer template available on the PJM website. Deposit based on PJM's new process.
14 | Customer decision point upon posting of study results to decide to proceed PJM Comment: this Design Component sounds like specific details of a Solution. Suggest revising to "Decision Points during Study Process". |  | There will be are decision points 1, 2, and 3 after Phases 1,2,3 of the Cycle Process. (PJM suggested edits.)
15 | GIA will be issued per current tariff requirements PJM Comment: this Design Component sounds like specific details of a Solution. Suggest revising to "GIA Requirements". |  | GIA issued for Replacement resource as part of the New Services Request Process, per the OATT sections covering the New Services Request Process
16 | Cost responsibility/allocation rules for any identified required network upgrades for Replacement Resource |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII) and network upgrades are cost allocated among all projects in a given Cycle if they meet PJM cost allocation thresholds as outlined in M14H, Att. B.
17 | Processing of existing Replacement Generation requests |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII)
18
19
20
21
22
23
24
25
26
27
28
29 | [8 empty] | Low
30 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3