## Scenario Feedback
Index | Submitted Scenario | Submitted Justificiation (if included) | Risk(s) (see 06/26/2019 FSSTF slides)
1 | Evaluate a full 90-day winter. | While the specific events (extreme weather and man-made infrastructure disruptions) that PJM analyzes may not last the whole winter, extremely stressful events can cause later resilience issues even after the event itself has passed. | Long Duration Cold Snap
2 | Examine infrastructure disruption scenarios lasting at least 90 days. | 14 days is not adequate to describe the potential duration of infrastructure disruptions. Major pipeline disruptions can and have in the past (i.e. 2016 Spectra disruption), lasted up to six months. | Natural Gas Pipeline Disruptions
3 | Run a case with concurrent peak load and infrastructure disruption during study period. Run a case with infrastructure outage during the entire 14 days. |  | Natural Gas Pipeline Disruptions; Long Duration Cold Snap; Short Duration Cold Snap
4 | Perform a sensitivity that varies the initial oil tank capability. | 85% assumption is higher compared to what units typically carry during the winter. Provide an alternate scenario that uses 50-60%, consistent with Navigant Consulting 2018 study. | Oil Refueling (Oil Terminal); Oil Refueling (Truck Restrictions)
5 | Perform sensitivities using different non-firm gas availability assumptions. ; Both firm and non-firm gas availability assumptions should be included at varying levels |  | Natural Gas Unavailability Non-Firm Units
6 | Cyber and physical risks informed by consultation with national security agencies |  | Cyber and physical risks (Phase 3 Analysis)
7 | Turbine technology failure scenario | All new turbine classes have to shut down during cold weather | Long Duration Cold Snap; Short Duration Cold Snap; Wind Intermittency (due to turbine settings)
8 | Regulatory driven nuclear shutdown |  | Nuclear Regulatory Shutdown (Fuel Related); Nuclear Regulatory Shutdown (Non-Fuel Related)
9 | No new pipelines are constructed |  | Natural Gas Pipeline Disruptions; Gas Unavailability Non-Firm Units
10 | Scenarios that assume more than 32.2 GW will retire | The March 2018 NETL report indicates that the retirement of aging coal and nuclear generation infrastructure may be underestimated. | Portfolio Senstivity
11 | Scenarios where the IRM is not met | We do not believe it is realistic to assume that replacement capacity will always match the pace of retirements. | Portfolio Senstivity
12 | Failure of multiple pipelines with multiple ruptures |  | Natural Gas Pipeline Disruptions
13 | An EMP or large cyber attack affecting electronics |  | Cyber and physical risks (Phase 3 Analysis)
14 | Scenarios that threaten energy security for the PJM region include hurricanes or other severe storms, which may cause flooding: - Nuclear plant shut down - Steam plant shut down - Wind turbine trips - Age related performance degradation, creating increased vulnerability - Common mode failures - Wet coal - Rail or barge transportation disruptions - Transmission outages | The likelihood of severe storms and flooding is increasing with climate change. High winds and flooding during storms have created a need for PJM nuclear plants to shut down. Flooding has a variety of impacts to steam plants due to their reliance on water for cooling and proximity to bodies of water. Flooding at a site may create a need to shut down a power plant or may disrupt fuel transportation. | Nuclear Regulatory Shutdown (Fuel Related); Nuclear Regulatory Shutdown (Non-Fuel Related); Coal Refueling (Bridge Failure); Coal Refueling (Lock and Dam Failure); Coal Refueling (Rail Failure); Coal Unavailability (Coal Quality); Oil Refueling (Oil Terminal); Oil Refueling (Truck Restrictions); Nuclear Unavailability (High Winds); Solar Intermittency; Wind Intermittency; Hurricane / Tropical Storms;
15 | Prolonged extreme heat may cause drought and/or elevated water temperatures: - Nuclear plant shut down - Steam plant shut down - Age related performance degradation, creating increased vulnerability - Common mode failures - High load | The likelihood of extreme heat is increasing with climate change. The steam power plants in PJM, including plants fueled by nuclear, coal, and gas, rely on cooling water. Water conditions may impact the ability of a steam plant to function. High water temperatures may affect a plant’s access to cooling water or ability to release water into a river or lake.3 Drought may limit access to cooling water. | Long Duration Heat Wave; Short Duration Heat Wave; Nuclear Regulatory Shutdown (Fuel Related); Nuclear Regulatory Shutdown (Non-Fuel Related); Hydro Unavailability (Drought / Low Water Level); High River Temperatures / Drought (Cooling Water Impacts)
16 | PJM has completed a study examining cold weather scenarios. To the extent that PJM’s previous study did not address all associated risks, the cold weather scenarios should be further evaluated. - Cold Snap - Nuclear plant shut down due to freezing - Steam plant shut down due to freezing - Wet or frozen coal - Age related performance degradation, creating increased vulnerability - Wind turbine blade icing - Frozen road, rail, or river conditions disrupting fuel transportation - Limits on natural gas availability due to gas heating load |  | Long Duration Cold Snap; Short Duration Cold Snap; Coal Refueling (Bridge Failure); Coal Refueling (Lock and Dam Failure); Coal Refueling (River Freezing); Coal Refueling (Rail Failure); Coal Unavailability (Coal Quality); Natural Gas Pipeline Disruptions; Natural Gas Unavailability Non-Firm Units Oil Refueling (Oil Terminal); Oil Refueling (Truck Restrictions); Nuclear Regulatory Shutdown (Fuel Related); Nuclear Regulatory Shutdown (Non-Fuel Related); Nuclear Unavailability (High Winds); Hydro Unavailability (Freezing Rivers); Solar Intermittency; Wind Intermittency; River Freezing (Cooling Water Impacts); Ice Storm (Transportation Impacts)
17 | Renewable energy growth and output should be assumed in the base case. | State renewable standards in the PJM region call for large increases in renewable generation. AWEA has provided updated data to PJM on the wind and solar energy and capacity requirements to meet the remaining demand under those standards, and the data are publicly available from each state. As these requirements are enacted in state law, the addition of sufficient renewable capacity to meet these standards should be assumed in most scenarios of the analysis. | Portfolio Senstivity
18 | All MWh of renewable energy should be included as contributing during stressed conditions | The analysis is focused on meeting load in all hours during extended cold snap conditions. Experience across the Northeast has revealed that events like last year’s Bomb Cyclone are at least partly driven by energy constraints, as finite amounts of oil – and in some cases gas and hydropower – are available given storage, transportation, and replenishment constraints. Because some fuels can be saved for later days and hours in these periods, every megawatt-hour of wind and solar produced during the period contributes to saving those fuels. Thus, every wind and solar MWh is providing equal value to every other MWh including nuclear, gas, and coal MWh in addressing those energy constraints. The analysis should incorporate this contribution, which is often higher than the MW-denominated capacity value calculated for wind and solar resources. That is because the energy-limited constraints are a different need than the instantaneous MW need that is typically studied in reliability analyses and in which dispatchability is particularly important. In this case the exact timing of the output is not important, as long as it is within the time frame of the cold snap condition. Wind and solar output can be estimated based on historical data sets and synthetic data sets that combine historical wind speeds and solar insolation with power output from current vintage wind and solar facilities to estimate future output during weather scenarios in question. We stand ready to assist in the acquisition of this data. | Wind Intermittency; Solar Intermittency
19 | PJM should assess the vulnerabilities that other fuel sources such as coal, nuclear and renewables face | It is important that PJM does not overlook recent occurrences in which fuel security has been jeopardized. During the 2019 polar vortex, PSEG’s 1,000 MW Salem Nuclear Plant reactor shuttered because ice clogged the screens that protected its cooling water intake. Although having onsite fuel available in the PJM region is helpful, it also jeopardizes fuel security during severe weather events or physical attacks. In recent major weather events, outages have been directly attributable to on-site fuel issues including frozen coal storage piles at coal-fired generation facilities and icing on wind turbine equipment. While PJM lists some risks such as river freezing, high winds and hurricanes, equipment and on-site fuel freezing should be considered as well. | Long Duration Cold Snap; Short Duration Cold Snap; Long Duration Heat Wave; Short Duration Heat Wave; Coal Refueling (Bridge Failure); Coal Refueling (Lock and Dam Failure); Coal Refueling (River Freezing); Coal Refueling (Rail Failure); Coal Unavailability (Coal Quality); Natural Gas Pipeline Disruptions; Natural Gas Unavailability Non-Firm Units Oil Refueling (Oil Terminal); Oil Refueling (Truck Restrictions); Nuclear Regulatory Shutdown (Fuel Related); Nuclear Regulatory Shutdown (Non-Fuel Related); Nuclear Unavailability (High Winds); Hydro Unavailability (Drought / Low Water Level); Hydro Unavailability (Freezing Rivers); Solar Intermittency; Wind Intermittency; High River Temperatures / Drought (Cooling Water Impacts); River Freezing (Cooling Water Impacts); Earthquake; Hurricane / Tropical Storms; Ice Storm (Transportation Impacts)