## Proposals
Project ID | Upgrade/Greenfield | Proposing Entity | Project Cost ($M) | Target Zone(s) | kV Level(s) | Analysis Type | FG# | Major Components/Project Description
2017_1-1A | Upgrade | Dominion | 4.52 | DOM | 230 | Gen Deliv - Summer | GD-S126, GD-S585, GD-S661 | Reconductor the existing Pleasant View - Ashburn - Beaumeade 230kV line (Line 274) with 1068 MVA conductor and replace line terminal equipment at Pleasant View, Ashburn, and Beaumeade.
2017_1-1B | Upgrade | Dominion | 7.11 | DOM | 230 | Gen Deliv - Summer | GD-S126, GD-S585, GD-S661 | Reconductor the existing Pleasant View - Ashburn -Beaumeade 230kV line (Line 274) with 1295 MVA conductor and replace line terminal equipment at Pleasant View, Ashburn, and Beaumeade.
2017_1-1C | Upgrade | Dominion | 3.05 | DOM | 230 | Gen Deliv - Summer | GD-S126, GD-S585, GD-S661 | Split Line #227 (Brambleton-Beaumeade) and termintate into existing belmont Substation
2017_1-1D | Upgrade | Dominion | 4.49 | DOM | 230 | Gen Deliv - Summer | GD-S107, GD-S159 | Reconductor the Woodbridge to Occoquan 230kV line segment of Line 2001 with 1047 MVA conductor and replace line terminal equipment at Possum Point, Woodbridge, and Occoquan.
2017_1-1E | Upgrade | Dominion | 4.96 | DOM | 230 | Gen Deliv - Summer | GD-S107, GD-S159 | Reconductor the Woodbridge to Occoquan 230kV line segment of Line 2001 with 1225 MVA conductor and replace line terminal equipment at Possum Point, Woodbridge, and Occoquan.
2017_1-1F | Upgrade | Dominion | 12.68 | DOM | 230 | Gen Deliv - Summer | GD-S107, GD-S159 | Rebuild the Woodbridge to Occoquan 230kV line segment of Line 2001. This segment of line is made up of double circuit 230kV structures, with Line 2001 and Line 215 sharing common structures. Line 215 from Woodbridge - Occoquan will be reconductored at the same time. Replace line terminal equipment at Possum Point, Woodbridge, and Occoquan.
2017_1-2A | Greenfield | Northeast Transmission Development | 39.1 | APS | 138 | Summer Gen Deliv; N-1 Thermal | GD-S579, GD-S587, GD-S596; N1-S175 | Build a single circuit 138 kV transmission line from the existing Waldo Run 138 kV substation to a new substation ("Glade Run") interconnecting the existing Harrison - Belmont 500 kV transmission line.
2017_1-2B | Greenfield | Northeast Transmission Development | 17 | APS | 138 | Summer Gen Deliv | GD-S857, GD-S578, GD-S582, GD-S584, GD-S577, GD-S581, GD-S583, GD-S44, GD-S53, GD-S766, GD-S787, GD-S765, GD-S786 | Build a single circuit 138 kV transmission line from the existing Logans Ferry 138 kV substation to a new substation ("Pucketa") interconnecting the existing Springdale - AA2-161 138 kV transmission line and the Springdale - Huntingdon 138 kV transmission line.
2017_1-2C | Greenfield | Northeast Transmission Development | 22.2 | APS | 138 | Summer Gen Deliv | GD-S857, GD-S578, GD-S582, GD-S584, GD-S577, GD-S581, GD-S583, GD-S44, GD-S53, GD-S766, GD-S787, GD-S765, GD-S786 | Build a single circuit 138 kV line from the existing Logans Ferry 138 kV substation to a new substation ("Pucketa") interconnecting the existing Springdale - AA2-161 138 kV transmission line and the Springdale - Federal Street 138 kV transmission line. Interconnect the remaining Pucketa - Federal Street 138 kV transmission line into the existing Schaffers Corner 138 kV substation.
2017_1-2D | Greenfield | Northeast Transmission Development | 64.8 | APS | 138 | Summer Gen Deliv | GD-S857, GD-S578, GD-S582, GD-S584, GD-S577, GD-S581, GD-S583, GD-S44, GD-S53, GD-S766, GD-S787, GD-S765, GD-S786 | Build a single circuit 345 kV transmission line from the existing Logans Ferry 345 kV substation to a new substation ("Thorn Run") interconnecting the existing South Bend - Yukon 500 kV transmission line.
2017_1-2E | Greenfield | Northeast Transmission Development | 12.7 | OVEC, DEOK | 138345 | Summer Gen Deliv; N-1 Thermal | GD-S763, GD-S746, GD-S814, GD-S745, GD-S813; N1-S91, N1-S92, N1-S126, N1-S155, N1-S156 | Build a 345 kV switching station ("Twelvemile") interconnecting the existing Silver Grove - Zimmer 345 kV transmission line and the Pierce - Buffington 345 kV transmission line
2017_1-3A | Greenfield | PSEG | 120.3 | APS | 138 | Summer Gen Deliv | GD-S44, GD-S53, GD-S857, GD-S578, GD-S582, GD-S584, GD-S581, GD-S583, GD-S577, GD-S766, GD-S787, GD-S765, GD-S786 | Tap the South Bend to Yukon 500kV line and build 500kV line to Logan's Ferry
2017_1-4A | Greenfield | Duquesne | 4.49 | APS | 138 | Summer Gen Deliv | GD-S577, GD-S578, GD-S581, GD-S582, GD-S583, GD-S584, GD-S587 | This proposal recommends the reconfiguration of the DLC-owned Cheswick-Plum and APS-owned Springdale-Wycoff-Yukon 138 kV circuits to create two (2) new tie lines between DLC and APS. These lines would be reconfigured to become the Cheswick-Wycoff-Yukon and Springdale-Plum 138 kV DLC-APS tie-lines. Once the lines are reconfigured, a portion of the newly established Springdale-Plum line would be reconductored.
2017_1-5A | Greenfield | Nextera | 30.1 | APS | 138 | Summer Gen Deliv; N-1 Thermal | GD-S579, GD-S587, GD-S596; N1-S175 | Build a new 500/138 kV substation connecting the following existing lines: Harrison-Belmont 500 kV and Harrison Reserve Tap-Glenn Falls 138 kV line.
2017_1-5B | Greenfield | Nextera | 11.7 | APS | 138 | Summer Gen Deliv | GD-S581, GD-S582, GD-S577, GD-S857, GD-S578, GD-S583, GD-S584 | Build a new 138 kV switching station (including a 5 ohm series reactor) connecting the following existing lines: Yukon-Charleroi 138 kV and Mitchell-Sheppler Hill JCT 138 kV line. Build new ~1 mile of 138 kV connecting new Miracle switching station to Wycoff Tap.
2017_1-5C | Greenfield | Nextera | 11.8 | APS | 138 | Summer Gen Deliv | GD-S581, GD-S582, GD-S577, GD-S857, GD-S578, GD-S583, GD-S584 | Build a new 138 kV switching station connecting the following existing lines: Yukon-Charleroi 138 kV and Mitchell-Sheppler Hill JCT 138 kV line. Build new ~1 mile of 138 kV connecting new Miracle switching station to Wycoff Tap. Reconductor Miracle – Mitchell 138 kV line
2017_1-6A | Upgrade | DEOK | 20.16 | OVEC, DEOK | 138345 | Summer Gen Deliv; N-1 Thermal | GD-S763, GD-S746, GD-S814, GD-S745, GD-S813; N1-S91, N1-S92, N1-S126, N1-S155, N1-S156 | The two existing 345/138kV transformers that connect Pierce 345kV Substation to Beckjord 138kV Substation are fed radially. This project will Reconfigure Pierce 345kV Substation by adding new breakers, moving a feeder, adding a third 345/138kV transformer, and feed the Pierce-Beckjord transformers in a breaker and a half or double bus configurations. The three transformer feeds will be distributed across the three sets of buses at Beckjord.
2017_1-7A | Greenfield | Transource | 29.46 | APS | 138 | Summer Gen Deliv | GD-S44, GD-S53, GD-S857, GD-S578, GD-S582, GD-S584, GD-S581, GD-S583, GD-S577, GD-S766, GD-S787, GD-S765, GD-S786 | Establish Barking Road 138kV switch station by cutting into the exisitng Logan’s Ferry – Highland 138kV line #2 and the Logan’s Ferry – Universal 138kV line. Establish Wright Road 138kV switch station by cutting into the exisitng Springdale – Huntingdon 138 kV line and the Springdale – Yukon 138 kV (via AA2-161 and Wycoff). Build the Barking Road - Wright Road 138 kV double circuit line.
2017_1-7B | Greenfield | Transource | 19.32 | AEP/DEOK | 345 | Winter Gen Deliv | GD-W3, GD-W5, GD-W6, GD-W7, GD-W8 | Construct new greenfield 345kV Switch Station to be called Anson Station. The existing Tanners Creek-East Bend 345kV, East Bend-Terminal 345kV and Miami Fort-Terminal 345kV circuits will all be looped in and out of this station. The station will be comprised of six new 345kV breakers and will be configured in a ring bus. Reconductor Tanners Creek-Anson 345kV.
2017_1-7C | Greenfield | Transource | 9.74 | DOM | 230 | Summer Gen Deliv | GD-S126, GD-S585, GD-S661 | Establish Sycolin Creek 230kV switch station by cutting into the exisitng Belmont – Pleasant View 230 kV line and the Brambleton – Cochrane Mill – Ashburn 230 kV line.
2017_1-7D | Greenfield | Transource | 55.09 | AEP/DEOK | 345 | Winter Gen Deliv | GD-W3, GD-W5, GD-W6, GD-W7, GD-W8 | Tap the Tanners Creek – Losantville 345 kV line and build a single circuit line approximately 16.8 miles to a new 345/138 station (Coyote) next to Willey.
2017_1-7E | Greenfield | Transource | 34.74 | APS | 138 | Summer Gen Deliv; N-1 Thermal | GD-S579, GD-S587, GD-S596; N1-S175 | Establish Narrow Run 500kV switch station by cutting into the exisitng Belmont - Harrison 500 kV line. Expand Waldo Run station and install a 500/138kV transformer. Build Narrow Run - Waldo Run 500kV line.
2017_1-7F | Greenfield | Transource | 11.45 | AEP/DEOK | 345 | Winter Gen Deliv | GD-W3, GD-W5, GD-W6, GD-W7, GD-W8 | Construct a parallel 345kV line from Tanners Creek to Miami Fort.
2017_1-7G | Greenfield | Transource | 9.91 | APS | 138 | Summer Gen Deliv | GD-S44, GD-S53, GD-S766, GD-S787, GD-S765, GD-S786 | Establish a new 138kV switch station near Seneca by cutting into the Markwest - Seneca 138kV line section. Construct a new 138kV line from the new station to McCalmont station.
2017_1-8A | Upgrade | AEP | 1.48 | AEP | 345 | Winter Gen Deliv | GD-W92 | Replace terminal equipiment on Maddox Creek-East Lima 345kV circuit.
2017_1-8B | Greenfield | AEP | 111.64 | AEP | 345 | Winter Gen Deliv | GD-W92 | Construct a new 345 kV single circuit line between Maddox Creek and Southwest Lima stations with 2-bundled 954 ACSR Cardinal conductor.
2017_1-8C | Upgrade | AEP | 1.2 | AEP | 345 | Winter Gen Deliv | GD-W3, GD-W5, GD-W6, GD-W7, GD-W8 | Upgrade existing 345kV terminal equipment at Tanners Creek station.
2017_1-9A | Upgrade | Exelon | 1.83 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Add Series Reactor at Claymont Substation (DPL) on Claymont to Linwood (PECO) 230 kV line.
2017_1-9B | Upgrade | Exelon | 28.4 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Rebuild Edge Moor (DPL) to Claymont (DPL) and Claymont (DPL) to Linwood (PECO) 230 kV Circuits
2017_1-9C | Upgrade | Exelon | 5.73 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Install Smart Wire solution at Claymont Substation (DPL) on the Claymont to Linwood (PECO) 230 kV Line.
2017_1-9D | Greenfield | Exelon | 37.95 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Construct new 230 kV line between Edge Moor (DPL) and Chichester (PECO) Substations
2017_1-9E | Greenfield | Exelon | 26.78 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Construct new 230 kV line between Edge Moor (DPL) and Linwood (PECO) Substations
2017_1-9F | Greenfield | Exelon | 28.69 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Construct new 230 kV line between Edge Moor (DPL) and Post (PECO) Substations
2017_1-9G | Greenfield | Exelon | 36.56 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Construct new substation near Linwood 230 kV Substation (PECO). Cut and connect existing 230 kV circuit (220-43) to new substation. Build new 230 kV circuit between Edge Moor (DPL) and new substation.
2017_1-9H | Greenfield | Exelon | 55.7 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Construct new 230 kV line between Harmony (DPL) and Linwood (PECO) Substations
2017_1-9I | Greenfield | Exelon | 64 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Construct new 230 kV line between Harmony (DPL) and Chichester (PECO) Substations
2017_1-9J | Greenfield | Exelon | 37.69 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Construct new 230 kV line between Harmony (DPL) and Clay (PECO) Substations
2017_1-9K | Upgrade | Exelon | 9.58 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Reconductor Edge Moor (DPL) - Claymont (DPL) and Claymont (DPL) - Linwood (PECO) 230 kV circuits with high temperature conductor.
2017_1-9L | Upgrade | Exelon | 1.4 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Replace the 230 kV CB #225 at Linwood Substation (PECO) with a double circuit breaker (back to back circuit breakers in one device).
2017_1-9M | Upgrade | Exelon | 8.37 | DPL/PECO | 230 | Summer gen Deliv | GD-S798, GD-S815 | Install at Phase Angle Regulator (PAR) at Claymont Substation (DPL) on Claymont (DPL) to Linwood (PECO) 230 kV Circuit
2017_1-9N | Greenfield | Exelon | 79.03 | DPL/ACE | 230 | Summer gen Deliv | GD-S798, GD-S815 | Construct new 230 kV line between Edge Moor (DPL) and Pedricktown (ACE) Substations
2017_1-10A | Upgrade | FirstEnergy | 7.08 | APS | 138 | Summer gen Deliv | GD-S581, GD-S582 | Reconductor Line with 954 ACSR Conductor, Replace Breaker Risers at Charleroi and Allenport
2017_1-10B | Upgrade | FirstEnergy | 3.19 | APS | 138 | Summer gen Deliv | GD-S857, GD-S578, GD-S584, GD-S577, GD-S583 | Reconductor the Yukon - Smithton - Shepler Hill Jct 138 kV Line with 795 ACSS Conductor, Replace Line Disconnect Switch at Yukon
2017_1-10C | Upgrade | FirstEnergy | 6.96 | APS | 138 | Summer gen Deliv | GD-S44, GD-S53, GD-S766, GD-S787, GD-S765, GD-S786 | Convert the existing 6 wire Butler - Shanor Manor - Krendale 138 kV Line into two separate 138 kV lines. New lines will be Butler - Keisters and Butler - Shanor Manor - Krendale 138 kV.
2017_1-10D | Upgrade | FirstEnergy | 0.12 | APS | 138 | Summer gen Deliv | GD-S857, GD-S578, GD-S584, GD-S577, GD-S583, GD-S582, GD-S581 | Replace the bus and line disconnect switches, bus taps, and bus conductor at the Cheswick Terminal at Springdale substation.
2017_1-10E | Upgrade | FirstEnergy | 2.69 | APS | 138 | Summer gen Deliv | GD-S857, GD-S578, GD-S584, GD-S577, GD-S583, GD-S582, GD-S581 | Reconductor the Springdale - Cheswick 138 kV Line and Upgrade the Terminal Equipment at Springdale
2017_1-10F | Greenfield | FirstEnergy | 23.4 | APS | 138 | Summer gen Deliv | GD-S857, GD-S578, GD-S584, GD-S577, GD-S583, GD-S582, GD-S581 | Construct Bunola Substation, Loop in the Mitchell - Wilson 138 kV Line, Construct Double Circuit 138 kV lines (~2.43 miles) to Wycoff Jct.-Wycoff section of Springdale - Wycoff Jct - Yukon 138 kV line. Reconductor/Install new conductor on ~1.7 miles of Wycoff Jct.-Wycoff line section.
2017_1-10G | Upgrade | FirstEnergy | 4.01 | APS | 138 | Summer Gen Deliv; N-1 Thermal | GD-S579, GD-S587, GD-S596; N1-S175 | Increase line ratings for 138 kV line segments from Pruntytown to White Hall Junction to Glen Falls. Pruntytown 138 kV Substation Terminal work on the White Hall Junction terminal to replace line relays and retain the existing carrier communitcation in order to increase line segment rating. Glen Falls 138 kV Substation Terminal work on the McAlpin terminal to upgrade bus risers and limiting conductor in order to increase line segment rating. McAlpin-White Hall Junction 138 kV Line Reconductor from structure #36-67 outside McAlpin substation to the 3-way junction (approximately 8.3 miles) to replace the existing 556 ACSR with 556 ACSS in order to increase line segment rating.
2017_1-10H | Upgrade | FirstEnergy | 11.1 | APS | 138 | Summer Gen Deliv; N-1 Thermal | GD-S579, GD-S587, GD-S596; N1-S175 | Separate the Shared Common Tower of the Pruntytown - Shinns Run 138 kV and the Pruntytown - Maple Lane 138 kV lines into two separate circuits utilizing the existing FirstEnergy ROW.
2017_1-10I | Greenfield | FirstEnergy | 40.06 | APS | 500, 138 | Summer Gen Deliv; N-1 Thermal | GD-S579, GD-S587, GD-S596; N1-S175 | Loop the Belmont - Harrison 500 kV line into the proposed Flint Run substation. Proposed location of substation is adjacent to existing line
2017_1-10J | Greenfield | FirstEnergy | 34.82 | APS | 138 | Summer Gen Deliv; N-1 Thermal | GD-S579, GD-S587, GD-S596; N1-S175 | Construct a new 138 kV line from Pruntytown to Glen Falls substations with 795 ACSR along new right-of-way approximately 15 miles. Pruntytown 138 kV Substation Install a new terminal and all necessary terminal equipment with the addition of a new 138 kV breaker designated at P21 for the new Glen Falls - Pruntytown 138 kV line. Glen Falls 138 kV Substation Install a new terminal on the east 138 kV bus with all necessary terminal equipment. Replace the #2 138-23 kV transformer to obtain space for the new terminal with a new 3-phase transformer, given that the #2 bank is a normally open, 3-1 phase transformer bank. Glen Falls - Pruntytown 138 kV Line Construct a new 138 kV line along new right-of-way approximately 15 miles with 795 ACSR.

## Included_Flowgates
Analysis | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | DC Ld(%) | AC Ld(%) | Contingency | Cont Type | Conductor Rating (MVA) | Comment
Sum 2022 N-1 Thermal | N1-S91 | 250086 | 08PIERCE | 249988 | 08BKJ135 | 1 | 138/138 | 212/212 | 498 | N/A | N/A | 112.0683 | 113.87 | 'AEP_P4_#6342_06PIERCE 345_P' | Line_FB | Rate A/B = 603/603 | Terminal equipment limited
Sum 2022 N-1 Thermal | N1-S92 | 250086 | 08PIERCE | 249988 | 08BKJ135 | 1 | 138/138 | 212/212 | 498 | N/A | N/A | 112.0683 | 113.87 | '.345.DEO&K-OVEC.C2 P_PIERCE' | Line_FB | Rate A/B = 603/603 | Terminal equipment limited
Sum 2022 N-1 Thermal | N1-S126 | 248013 | 06PIERCE | 250143 | 08PRCE18 | 18 | 345/138 | 206/212 | 501 | N/A | N/A | 108.982 | 108.1851 | '.345.DEO&K.C2 R_PIERCE' | Line_FB | Transformer
Sum 2022 N-1 Thermal | N1-S155 | 248013 | 06PIERCE | 250086 | 08PIERCE | 17 | 345/138 | 206/212 | 537 | N/A | N/A | 104.041 | 103.143 | 'AEP_P4_#6342_06PIERCE 345_P' | Line_FB | Transformer
Sum 2022 N-1 Thermal | N1-S156 | 248013 | 06PIERCE | 250086 | 08PIERCE | 17 | 345/138 | 206/212 | 537 | N/A | N/A | 104.041 | 103.143 | '.345.DEO&K-OVEC.C2 P_PIERCE' | Line_FB | Transformer
Sum 2022 N-1 Thermal | N1-S175 | 235442 | 01MCALPN | 235334 | 01GLENFL | 1 | 138/138 | 201/201 | 229 | N/A | N/A | 97.7729 | 100.72 | 'AP-P7-1-MP-138-019' | Tower | Rate B =268 | Terminal equipment limited
Sum 2022 GD/CMO | GD-S763 | 248013 | 06PIERCE | 250143 | 08PRCE18 | 18 | 345/138 | 206/212 | 501 | 552.05 | 547.53 | 110.19 | 109.28 | '.345.DEO&K.C2 R_PIERCE' | breaker | Transformer
Sum 2022 GD/CMO | GD-S746 | 250086 | 08PIERCE | 249988 | 08BKJ135 | 1 | 138/138 | 212/212 | 498 | 562.63 | 571.03 | 112.9779 | 114.6647 | '.345.DEO&K-OVEC.C2 P_PIERCE' | breaker | Rate A/B = 603/603 | Terminal equipment limited
Sum 2022 GD/CMO | GD-S814 | 248013 | 06PIERCE | 250086 | 08PIERCE | 17 | 345/138 | 206/212 | 537 | 563.23 | 557.84 | 104.88 | 103.88 | '.345.DEO&K-OVEC.C2 P_PIERCE' | breaker | Transformer
Sum 2022 GD/CMO | GD-S745 | 250086 | 08PIERCE | 249988 | 08BKJ135 | 1 | 138/138 | 212/212 | 498 | 562.63 | 571.03 | 112.9779 | 114.6647 | 'AEP_P4_#6342_06PIERCE 345_P' | breaker | Rate A/B = 603/603 | Terminal equipment limited
Sum 2022 GD/CMO | GD-S813 | 248013 | 06PIERCE | 250086 | 08PIERCE | 17 | 345/138 | 206/212 | 537 | 563.23 | 557.84 | 104.88 | 103.88 | 'AEP_P4_#6342_06PIERCE 345_P' | breaker | Transformer
Sum 2022 GD/CMO | GD-S44 | 235152 | 01BUTLER | 235246 | 01SHANOR | 1 | 138/138 | 201/201 | 452 | 540.31 | 529.12 | 119.5383 | 117.062 | 'AP-P1-2-WP-500-302T' | single | Same as basecase
Sum 2022 GD/CMO | GD-S53 | 235246 | 01SHANOR | 235205 | 01KRENDL | 1 | 138/138 | 201/201 | 452 | 527.01 | 517.29 | 116.5958 | 114.4444 | 'AP-P1-2-WP-500-302T' | single | Same as basecase
Sum 2022 GD/CMO | GD-S857 | 235277 | 01YUKON | 235252 | 01SMTH62 | 1 | 138/138 | 201/201 | 376 | 383.18 | 378.18 | 101.9102 | 100.5804 | 'AP-P2-3-WP-138-204' | breaker | Same as basecase
Sum 2022 GD/CMO | GD-S579 | 235442 | 01MCALPN | 235334 | 01GLENFL | 1 | 138/138 | 201/201 | 229 | 248.40 | 255.20 | 108.473 | 111.4424 | 'AP-P7-1-MP-138-019' | tower | Rate B =268 | Terminal equipment limited
Sum 2022 GD/CMO | GD-S587 | 235391 | 01PRNTY | 235426 | 01WHITEH | 1 | 138/138 | 201/201 | 287 | 296.47 | 300.77 | 103.3013 | 104.7995 | 'AP-P7-1-MP-138-019' | tower | Rate B = 376 | Terminal equipment limited
Sum 2022 GD/CMO | GD-S596 | 235426 | 01WHITEH | 235442 | 01MCALPN | 1 | 138/138 | 201/201 | 268 | 268.90 | 274.9 | 100.337 | 102.5758 | 'AP-P7-1-MP-138-019' | tower | Same as basecase
Sum 2022 GD/CMO | GD-S578 | 235277 | 01YUKON | 235252 | 01SMTH62 | 1 | 138/138 | 201/201 | 376 | 419.73 | 414.53 | 111.6313 | 110.2483 | 'AP-P7-1-WPP-138-78' | tower | Same as basecase
Sum 2022 GD/CMO | GD-S582 | 235135 | 01ALLENP | 235161 | 01CHARLR | 1 | 138/138 | 201/201 | 179 | 195.27 | 192.57 | 109.0912 | 107.5828 | 'AP-P7-1-WPP-138-78' | tower | Rate B =192 | Geographically proximate with other violations
Sum 2022 GD/CMO | GD-S584 | 235252 | 01SMTH62 | 235247 | 01SHEPLR | 1 | 138/138 | 201/201 | 376 | 406.63 | 402.73 | 108.1472 | 107.11 | 'AP-P7-1-WPP-138-78' | tower | Same as basecase
Sum 2022 GD/CMO | GD-S577 | 235277 | 01YUKON | 235252 | 01SMTH62 | 1 | 138/138 | 201/201 | 376 | 424.83 | 419.63 | 112.9877 | 111.6047 | 'AP-P7-1-WPP-138-80' | tower | Same as basecase
Sum 2022 GD/CMO | GD-S581 | 235135 | 01ALLENP | 235161 | 01CHARLR | 1 | 138/138 | 201/201 | 179 | 198.47 | 195.67 | 110.8789 | 109.3147 | 'AP-P7-1-WPP-138-80' | tower | Rate B =192 | Geographically proximate with other violations
Sum 2022 GD/CMO | GD-S583 | 235252 | 01SMTH62 | 235247 | 01SHEPLR | 1 | 138/138 | 201/201 | 376 | 411.73 | 407.73 | 109.5036 | 108.4398 | 'AP-P7-1-WPP-138-80' | tower | Same as basecase
Sum 2022 GD/CMO | GD-S766 | 235152 | 01BUTLER | 235246 | 01SHANOR | 1 | 138/138 | 201/201 | 452 | 512.49 | 504.51 | 113.3832 | 111.6164 | 'ATSI-P2-3-OEE-138-138T' | breaker | Same as basecase
Sum 2022 GD/CMO | GD-S787 | 235246 | 01SHANOR | 235205 | 01KRENDL | 1 | 138/138 | 201/201 | 452 | 499.19 | 492.69 | 110.4407 | 109.0012 | 'ATSI-P2-3-OEE-138-138T' | breaker | Same as basecase
Sum 2022 GD/CMO | GD-S765 | 235152 | 01BUTLER | 235246 | 01SHANOR | 1 | 138/138 | 201/201 | 452 | 512.49 | 504.51 | 113.3832 | 111.6164 | 'ATSI-P2-3-OEE-138-139T' | breaker | Same as basecase
Sum 2022 GD/CMO | GD-S786 | 235246 | 01SHANOR | 235205 | 01KRENDL | 1 | 138/138 | 201/201 | 452 | 499.19 | 492.69 | 110.4407 | 109.0012 | 'ATSI-P2-3-OEE-138-139T' | breaker | Same as basecase
Sum 2022 GD/CMO | GD-S107 | 314094 | 6WOODBR | 314067 | 6OCCOQUN | 1 | 230/230 | 345/345 | 678.68 | 696.66 | 713.98 | 102.649 | 105.2011 | 'DVP_P1-2: LN 215' | single | Same as basecase
Sum 2022 GD/CMO | GD-S159 | 314074 | 6POSSUM | 314094 | 6WOODBR | 1 | 230/230 | 345/345 | 749.18 | 753.36 | 763.24 | 100.5577 | 101.8769 | 'DVP_P1-2: LN 215' | single | Rate B = 1047 | Terminal equipment limited
Sum 2022 GD/CMO | GD-S126 | 314072 | 6PL VIEW | 314004 | 6ASHBURN | 1 | 230/230 | 345/345 | 716.28 | 732.85 | 741.49 | 102.3127 | 103.5198 | 'DVP_P1-2: LN 2172' | single | Same as basecase
Sum 2022 GD/CMO | GD-S585 | 314072 | 6PL VIEW | 314004 | 6ASHBURN | 1 | 230/230 | 345/345 | 877 | 936.39 | 936.83 | 106.772 | 106.8224 | 'DVP_P7-1: LN 2172-2183' | tower | Same as basecase
Sum 2022 GD/CMO | GD-S798 | 231000 | CLAY_230 | 213750 | LINWOOD | 1 | 230/230 | 235/230 | 804 | 868.57 | 859.13 | 108.0309 | 106.8565 | 'PECO_P4_LINWO225/* $ DELCO $ LINWO225 $ STBK' | breaker | DPL is Same as basecase, PECO Rate A/B = 731/885
Sum 2022 GD/CMO | GD-S815 | 231001 | EDGEMR 5 | 231000 | CLAY_230 | 1 | 230/230 | 235/235 | 804 | 863.35 | 852.50 | 107.3822 | 106.0327 | 'PECO_P4_LINWO225/* $ DELCO $ LINWO225 $ STBK' | breaker | Same as basecase
Sum 2022 GD/CMO | GD-S661 | 314004 | 6ASHBURN | 314010 | 6BEAMEAD | 1 | 230/230 | 345/345 | 877 | 894.11 | 895.25 | 101.95 | 102.08 | 'DVP_P7-1: LN 2172-2183' | tower |  | New violation added as part of V2 update
Winter 2022 GD/CMO | GD-W3 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345/345 | 205/212 | 2022 | 2238.22 | 2238.22 | 110.6934 | 110.6934 | '.345.DEO&K.B2 TERMINAL-EAST BEND 4516' | single | AEP = 2550/2550, DEOK=2406/2406 | Terminal equipment limited
Winter 2022 GD/CMO | GD-W5 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345/345 | 205/212 | 2022 | 2078.78 | 2082.55 | 102.8081 | 102.9946 | 'AEP_P1-2_#7441' | single | AEP = 2550/2550, DEOK=2406/2406 | Terminal equipment limited
Winter 2022 GD/CMO | GD-W6 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345/345 | 205/212 | 2022 | 2011.99 | 2011.99 | 99.5049 | 99.5049 | 'AEP_P1-2_#1358' | single | AEP = 2550/2550, DEOK=2406/2406 | Terminal equipment limited
Winter 2022 GD/CMO | GD-W7 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345/345 | 205/212 | 2022 | 1982.85 | 1975.09 | 98.0638 | 97.68 | '.345.DEO&K-OVEC.B2 FOSTER-PIERCE 4502' | single | AEP = 2550/2550, DEOK=2406/2406 | Terminal equipment limited
Winter 2022 GD/CMO | GD-W8 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345/345 | 205/212 | 2022 | 1982.85 | 1975.09 | 98.0638 | 97.68 | 'AEP_P1-2_#876' | single | AEP = 2550/2550, DEOK=2406/2406 | Terminal equipment limited
Winter 2022 GD/CMO | GD-W92 | 246929 | 05MADDOX | 242935 | 05E LIMA | 1 | 345/345 | 205/205 | 1286 | 1316.11 | 1327.57 | 102.3411 | 103.2328 | 'AEP_P1-2_#7441' | single | A/B = 2550/2550 | Terminal equipment limited

## Excluded_Flowgates
Flowgates Excluded from the 2017_1 Proposal Window
Analysis | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Contingency | Cont Type | Conductor Rating (MVA) | Comment
Summer 2022 N-1 Thermal | N1-S131 | 235506 | 01RINGLD | 235505 | 01RINGLD | 4 | 230/138 | 201/201 | 398 | 109.6231 | 109.55 | 'AP-P2-3-PE-230-001A' | Line_FB | Transformer
Summer 2022 N-1 Thermal | N1-S132 | 235506 | 01RINGLD | 235505 | 01RINGLD | 4 | 230/138 | 201/201 | 398 | 105.9548 | 105.86 | 'AP-P2-3-PE-230-002B' | Line_FB | Transformer
Summer 2022 N-1 Thermal | N1-S134 | 235506 | 01RINGLD | 235505 | 01RINGLD | 3 | 230/138 | 201/201 | 398 | 109.6231 | 109.55 | 'AP-P2-3-PE-230-001B' | Line_FB | Transformer
Summer 2022 N-1 Thermal | N1-S135 | 235506 | 01RINGLD | 235505 | 01RINGLD | 3 | 230/138 | 201/201 | 398 | 105.9548 | 105.86 | 'AP-P2-3-PE-230-002A' | Line_FB | Transformer
Winter 2022 N-1 Thermal | N1-WT43 | 235506 | 01RINGLD | 235505 | 01RINGLD | 4 | 230/138 | 201/201 | 398 | 105.9296 | 106.06 | 'AP-P2-3-PE-230-001A' | Line_FB | Transformer
Winter 2022 N-1 Thermal | N1-WT44 | 235506 | 01RINGLD | 235505 | 01RINGLD | 4 | 230/138 | 201/201 | 398 | 100.6281 | 101.04 | 'AP-P2-3-PE-230-002B' | Line_FB | Transformer
Winter 2022 N-1 Thermal | N1-WT46 | 235506 | 01RINGLD | 235505 | 01RINGLD | 3 | 230/138 | 201/201 | 398 | 105.9296 | 106.06 | 'AP-P2-3-PE-230-001B' | Line_FB | Transformer
Winter 2022 N-1 Thermal | N1-WT47 | 235506 | 01RINGLD | 235505 | 01RINGLD | 3 | 230/138 | 201/201 | 398 | 100.6281 | 101.04 | 'AP-P2-3-PE-230-002A' | Line_FB | Transformer
Analysis | FG # | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper Limit | Violation | Cont Type |  | Contingency | Comment
Summer 2022 N-1 Voltage | N1-SVH1 | 200930 | 26MAINESBURG | 345 | 226 | 1.0505 | 1.0446 | 1.05 | H | Bus |  | PN-P2-2-PN-345-003 | Immediate Need
Summer 2022 N-1 Voltage | N1-SVH2 | 200930 | 26MAINESBURG | 345 | 226 | 1.0506 | 1.0446 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-84C1 | Immediate Need
Summer 2022 N-1 Voltage | N1-SVH3 | 200930 | 26MAINESBURG | 345 | 226 | 1.0506 | 1.0446 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-84D1 | Immediate Need
Summer 2022 N-1 Voltage | N1-SVH4 | 200930 | 26MAINESBURG | 345 | 226 | 1.0506 | 1.0446 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-84A1 | Immediate Need
Summer 2022 N-1 Voltage | N1-SVH5 | 200930 | 26MAINESBURG | 345 | 226 | 1.0554 | 1.0446 | 1.05 | H | Line_FB |  | PN-P2-3-PN-345-8E1T | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH1 | 200930 | 26MAINESBURG | 345 | 226 | 1.052 | 1.0509 | 1.05 | H | Tower |  | PS-P7-1_5063+T2298 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH2 | 200930 | 26MAINESBURG | 345 | 226 | 1.052 | 1.0509 | 1.05 | H | Tower |  | PS-P7-1_5063+N2214 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH3 | 200930 | 26MAINESBURG | 345 | 226 | 1.0523 | 1.0509 | 1.05 | H | Tower |  | PL:03:P71:001017 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH4 | 200930 | 26MAINESBURG | 345 | 226 | 1.0523 | 1.0509 | 1.05 | H | Bus |  | PL:03:P21:000300 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH5 | 200930 | 26MAINESBURG | 345 | 226 | 1.0536 | 1.0509 | 1.05 | H | Bus |  | PN-P2-2-PN-115-065 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH6 | 200930 | 26MAINESBURG | 345 | 226 | 1.0537 | 1.0509 | 1.05 | H | Bus |  | PN-P2-2-PN-115-064 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH7 | 200930 | 26MAINESBURG | 345 | 226 | 1.0541 | 1.0509 | 1.05 | H | Single |  | PN-P1-2-PN-115-036B | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH8 | 200930 | 26MAINESBURG | 345 | 226 | 1.0543 | 1.0509 | 1.05 | H | Single |  | PN-P1-2-PN-115-103 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH9 | 200930 | 26MAINESBURG | 345 | 226 | 1.0543 | 1.0509 | 1.05 | H | Single |  | PN-P1-2-PN-230-013 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH10 | 200930 | 26MAINESBURG | 345 | 226 | 1.0571 | 1.0509 | 1.05 | H | Single |  | PN-P1-3-PN-345-001 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH11 | 200930 | 26MAINESBURG | 345 | 226 | 1.0571 | 1.0509 | 1.05 | H | Bus |  | PN-P2-2-PN-345-003 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH12 | 200930 | 26MAINESBURG | 345 | 226 | 1.0574 | 1.0509 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-84C1 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH13 | 200930 | 26MAINESBURG | 345 | 226 | 1.0574 | 1.0509 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-84D1 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH14 | 200930 | 26MAINESBURG | 345 | 226 | 1.0574 | 1.0509 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-84A1 | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH15 | 200930 | 26MAINESBURG | 345 | 226 | 1.058 | 1.0509 | 1.05 | H | Line_FB |  | PN-P2-3-PN-345-8E1T | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH16 | 200930 | 26MAINESBURG | 345 | 226 | 1.058 | 1.0509 | 1.05 | H | Single |  | PN-P1-2-PN-345-104T | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH17 | 200930 | 26MAINESBURG | 345 | 226 | 1.0819 | 1.0509 | 1.05 | H | Line_FB |  | PN-P2-3-PN-345-8F1T | Immediate Need
Winter 2022 N-1 Voltage | N1-WVH18 | 200929 | 26MAINESBURG | 115 | 226 | 1.0508 | 1.0358 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-84C1 | Immediate Need
Analysis | FG # | Contingency Name |  | Cont. Type | Cont. Areas | Isolated Load (MW) | MW Drop | Comment
Summer N-1 Load Drop | N1-SLD1 | COMED_P7_138-L4605__R-N_+_138-L4606__B-N |  | Tower | 222 | 351.5 | 351.5 | Immediate Need
Analysis | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld (%) | AC Ld (%) | Contingency 1 | Contingency 2 |  |  | Conductor Rating (MVA) | Comment
Summer N-1-1 Thermal | N2-ST1 | 228110 | BLE | 228111 | MDLE TP | 1 | 138/138 | 234/234 | 219.0 | 102.968 | 108.2 | 'AE_P1-2 CUMB-DENN' | 'AE_P1-2 CORSON-UNION' |  |  | Same as basecase
Summer N-1-1 Thermal | N2-ST2 | 235506 | 01RINGLD | 235505 | 01RINGLD | 4 | 230/138 | 201/201 | 398.0 | 101.9095 | 101.23 | 'AP-P1-3-PE-230-004' | 'BG_P1_5013' |  |  | Transformer
Summer N-1-1 Thermal | N2-ST3 | 235506 | 01RINGLD | 235505 | 01RINGLD | 3 | 230/138 | 201/201 | 398.0 | 101.9095 | 101.23 | 'AP-P1-3-PE-230-005' | 'BG_P1_5013' |  |  | Transformer
Summer N-1-1 Thermal | N2-ST4 | 228110 | BLE | 228111 | MDLE TP | 1 | 138/138 | 234/234 | 219.0 | 103.1963 | 108.2 | 'AE_P1-2 CORSON-UNION' | 'AE_P1-2 CUMB-DENN' |  |  | Same as basecase
Summer N-1-1 Thermal | N2-ST8 | 235506 | 01RINGLD | 235505 | 01RINGLD | 3 | 230/138 | 201/201 | 398.0 | 100.8543 | 101.09 | 'BG_P1_5013' | 'AP-P1-3-PE-230-005' |  |  | Transformer
Summer N-1-1 Thermal | N2-ST9 | 235506 | 01RINGLD | 235505 | 01RINGLD | 4 | 230/138 | 201/201 | 398.0 | 100.8543 | 101.09 | 'BG_P1_5013' | 'AP-P1-3-PE-230-004' |  |  | Transformer
Summer N-1-1 Thermal | N2-ST13 | 217011 | MAYWOOD_1 | 217921 | SADDLEBRK_2 | 1 | 230/230 | 231/231 | 400.0 | 101.75 | 101.71 | 'PS_P1-2_P-2294' | 'BASE CASE' |  |  |  | Immediate Need
Analysis | FG # | Bus # | Name | kV | Area | Cont Volt | Base Volt | Lower Limit | Violation |  | OTDF(%) | Contingency
Summer Load Deliv | LD-SVL1 | 232253 | FIVE PTS | 69 | 40 | 0.9418 | 0.9855 | 0.942 | L |  | 5.068 | DPL_P1_3_COOLSPG AT20
Summer Load Deliv | LD-SVL2 | 232805 | ROBINSON | 138 | 40 | 0.9394 | 1.0107 | 0.942 | L |  | 6.377 | DPL_P1_2_CKT 13705
Summer Load Deliv | LD-SVL3 | 232120 | REHOBOTH | 138 | 40 | 0.9409 | 1.0033 | 0.942 | L |  | 5.486 | DPL_P1_2_CKT 13705
Analysis | FG # | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper Limit | Violation | Cont Type |  | Contingency | Comment
N-1 Light Load Voltage | N1-LLVH1 | 200930 | 26MAINESBURG | 345 | 226 | 1.0523 | 1.0507 | 1.05 | H | Bus |  | PN-P2-2-PN-115-070 | Immediate Need
N-1 Light Load Voltage | N1-LLVH2 | 200930 | 26MAINESBURG | 345 | 226 | 1.0523 | 1.0507 | 1.05 | H | Tower |  | PECO_P7-1_220-0607/* $ CHESCO $ 220-0607 $ DCT | Immediate Need
N-1 Light Load Voltage | N1-LLVH3 | 200930 | 26MAINESBURG | 345 | 226 | 1.0524 | 1.0507 | 1.05 | H | Bus |  | PN-P2-2-PN-115-072 | Immediate Need
N-1 Light Load Voltage | N1-LLVH4 | 200930 | 26MAINESBURG | 345 | 226 | 1.0525 | 1.0507 | 1.05 | H | Bus |  | PN-P2-2-PN-115-065 | Immediate Need
N-1 Light Load Voltage | N1-LLVH5 | 200930 | 26MAINESBURG | 345 | 226 | 1.0537 | 1.0507 | 1.05 | H | Tower |  | PS-P7-1_5063+N2214 | Immediate Need
N-1 Light Load Voltage | N1-LLVH6 | 200930 | 26MAINESBURG | 345 | 226 | 1.0537 | 1.0507 | 1.05 | H | Tower |  | PS-P7-1_5063+T2298 | Immediate Need
N-1 Light Load Voltage | N1-LLVH7 | 200930 | 26MAINESBURG | 345 | 226 | 1.055 | 1.0507 | 1.05 | H | Bus |  | PN-P2-2-PN-345-003 | Immediate Need
N-1 Light Load Voltage | N1-LLVH8 | 200930 | 26MAINESBURG | 345 | 226 | 1.0551 | 1.0507 | 1.05 | H | Tower |  | PL:03:P71:001017 | Immediate Need
N-1 Light Load Voltage | N1-LLVH9 | 200930 | 26MAINESBURG | 345 | 226 | 1.0571 | 1.0507 | 1.05 | H | Single |  | PN-P1-2-PN-345-104T | Immediate Need
N-1 Light Load Voltage | N1-LLVH10 | 200930 | 26MAINESBURG | 345 | 226 | 1.0573 | 1.0507 | 1.05 | H | Single |  | PN-P1-2-PN-230-101T | Immediate Need
N-1 Light Load Voltage | N1-LLVH11 | 200930 | 26MAINESBURG | 345 | 226 | 1.065 | 1.0507 | 1.05 | H | Single |  | PN-P1-2-PN-230-013 | Immediate Need
N-1 Light Load Voltage | N1-LLVH12 | 200930 | 26MAINESBURG | 345 | 226 | 1.0668 | 1.0507 | 1.05 | H | Line_FB |  | PL:P42:001060 | Immediate Need
N-1 Light Load Voltage | N1-LLVH13 | 200930 | 26MAINESBURG | 345 | 226 | 1.0668 | 1.0507 | 1.05 | H | Line_FB |  | PL:P42:000445 | Immediate Need
N-1 Light Load Voltage | N1-LLVH14 | 200930 | 26MAINESBURG | 345 | 226 | 1.0668 | 1.0507 | 1.05 | H | Single |  | PN-P1-2-PN-230-102T | Immediate Need
N-1 Light Load Voltage | N1-LLVH15 | 200930 | 26MAINESBURG | 345 | 226 | 1.0668 | 1.0507 | 1.05 | H | Single |  | PL:P13:100352 | Immediate Need
N-1 Light Load Voltage | N1-LLVH16 | 200930 | 26MAINESBURG | 345 | 226 | 1.0671 | 1.0507 | 1.05 | H | Line_FB |  | PN-P2-3-PN-230-17T | Immediate Need
N-1 Light Load Voltage | N1-LLVH17 | 200930 | 26MAINESBURG | 345 | 226 | 1.0672 | 1.0507 | 1.05 | H | Bus |  | PL:03:P21:000300 | Immediate Need
N-1 Light Load Voltage | N1-LLVH18 | 200930 | 26MAINESBURG | 345 | 226 | 1.0693 | 1.0507 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-46FT | Immediate Need
N-1 Light Load Voltage | N1-LLVH19 | 200929 | 26MAINESBURG | 115 | 226 | 1.0503 | 1.0385 | 1.05 | H | Line_FB |  | PN-P2-3-PN-115-46FT | Immediate Need
Analysis | FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | Cont Label | Cont Type | FN DC % | FN AC % | Conductor Rating (MVA) | PJM Comment
Winter Gen Deliv | GD-W37 | 219050 | VFT_1 | 219049 | WARINICO_1 | 1 | 230/230 | 231/231 | 924 | 1131.57 | 1159.96 | 'PS_P1-2_R-2218_LT' | single | 122.4642 | 125.5365 | same as the basecase | AC Loading should be around 105.5% without retired generators contribution (Hudson 618 MW and Bayonne 158 MW)
Winter Gen Deliv | GD-W38 | 219050 | VFT_1 | 219049 | WARINICO_1 | 1 | 230/230 | 231/231 | 924 | 1123.17 | 1152.13 | 'PS_P1-2_R-2218' | single | 121.5552 | 124.6898 | same as the basecase | AC Loading should be around 104.76% without retired generators contribution (Hudson 618 MW and Bayonne 158 MW)
Winter Gen Deliv | GD-W39 | 219050 | VFT_1 | 219049 | WARINICO_1 | 1 | 230/230 | 231/231 | 767 | 869.94 | 907.69 | Base Case | single | 113.4218 | 118.3425 | same as the basecase | AC Loading should be around 103.65% without retired generators contribution (Hudson 618 MW and Bayonne 158 MW)
Winter Gen Deliv | GD-W348 | 219050 | VFT_1 | 219049 | WARINICO_1 | 1 | 230/230 | 231/231 | 924 | 1219.74 | 1254.91 | 'PS_P7-1_G2207+R2218' | tower | 132.0065 | 135.8132 | same as the basecase | AC Loading should be around 112.7% without retired generators contribution (Hudson 618 MW and Bayonne 158 MW)
Winter Gen Deliv | GD-W353 | 218316 | WARINICO_2 | 217122 | ALDENE_4 | 1 | 230/230 | 231/231 | 980 | 1173.24 | 1214.78 | 'PS_P7-1_G2207+R2218' | tower | 119.7184 | 123.9572 | same as the basecase | AC Loading should be around 102.14% without retired generators contribution (Hudson 618 MW and Bayonne 158 MW)
Note:
| PJM Not Accepting Proposals |  | The facilities are overloaded in the near term and an immediate need upgrade is required to resolve the violations.
Excluded from window (See PJM Operating Agreement 1.5.8(n) Reliability Violations on Transmission Facilities Below 200 kV)

## Terms
I. Terminology
For Proposal windows, PJM will distribute an electronic workbook of potential violations on facilities identified through a series of analyses. The following column headings are generally representative of the data fields that will be used to identify the specific facility and other factors of the output of this analysis. Not all column headings will appear in every sheet within the workbook. Additional information deemed necessary by PJM will be provided on a separate sheet along with the results file.
Typical thermal analysis column headings:
Column Headings | Title | Description
FG # | Flowgate Number | A sequential numbering of the identified potential violations
Fr Bus | From Bus Number | PSSE model Bus number corresponding to one end of line identified as a potential violation
Fr Name | From Bus Name | PSSE model Bus name corresponding to one end of line identified as a potential violation
To Bus | To Bus Number | PSSE model Bus number corresponding to other end of line identified as a potential violation
To Name | To Bus Name | PSSE model Bus name corresponding to other end of line identified as a potential violation
Monitored Facility | Monitored Facility | The circuit on which a potential violation is occurring
Base Rate (MVA) | Base Rate (MVA) | Normal Facility Rating (Rate A)
% Overload | Percentage Overload | Percentage above base rate
CKT | Circuit | Circuit number of identified potential violation
KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Rating | Line Rating | Applicable Thermal rating (MVA) of line
DC Ld(%) | Direct Current Loading percentage | Percentage above 'Line Rating' determined from DC testing
AC Ld(%) | Alternating Current Loading percentage | Percentage above 'Line Rating' determined from AC testing
Cont Type | Contingency Type | Contingency Categorization (potential options include: Single, Bus, Line_FB, Tower)
Cont Name | Contingency Name | Contingency Name as identified in associated contingency file or embedded in the spreadsheet
Contingency | Contingency | Contingency Description
Violation Date | Violation Date | Date on which violation is expected to occur
Analysis Case | Analysis Case | Case title to use in replicating analysis
Typical voltage analysis column headings:
Column Headings | Title | Description
FG # | Flowgate Number | A sequential numbering of the identified potential violations
Bus # | Bus Number | PSSE model Bus number corresponding to bus identified as a potential violation
Name | Bus Name | PSSE model Bus name corresponding to bus identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
Low Limit | Low Voltage Limit(P.U.) | Threshold of Per Unit Low voltage, if ContVolt is under this limit, a potential violation is identified
Upper Limit | High Voltage Limit(P.U.) | Threshold of Per Unit High voltage, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency Categorization (potential options include: Single, Bus, Line_FB, Tower)
Vdrop(%) | Voltage drop | The Percentage that the voltage has dropped as a result of the contingency
Contingency | Contingency Name | Contingency Name as identified in associated contingency file
Contingency 1 | First Contingency | N-1 (First) Contingency identified
Contingency 2 | Second Contingency | N-1-1 (Second) contingency identified in N-1-1 analysis
Violation Date | Violation Date | Date on which violation is expected to occur
Analysis Case | Analysis Case | Case title to use in replicating analysis