## CT Heat Rate Curves
Minimum Load
Base Load
Peak Load
Fuel Cost = $4 mmBtu
VOM = $75/EOH
No Load Cost = No Load Fuel x Fuel Cost
= $ 2,359/hr

## CT Heat Input
Fitted Regression Line Equation
No Load Fuel = 578.23 mmBtu/hr
Minimum Load
Base Load
Peak Load

## CT
Combustion Turbine Heat Rate & Cost Curves
Heat Rate Curves
Output | Heat Input | Heat Rate | Incrementals
(MW) | (MBtu/hr) | (Btu/kWh) | (Btu/kWh)
0 | 578.23 |  |  | No Load
70 | 879.02 | 12557.4286 | 4297 | Min
90 | 1054.57 | 11717.4444 | 8777.5 | Base
100 | 1157.28 | 11572.8 | 10271 | Peak
Conditions at 59F
a= | 578.23 | (No Load Fuel) |  |  |  | Fuel Cost | 4 | $/mmBtu
b= | 0.8122 |  |  |  |  | VOM | 75 | $/EOH
c= | 0.0498 |  |  |  |  | PF | 1.02
Gas |  |  | Maintenance |  | Operating | Incremental | No Load = | 2359.1784 | $/hr
Net Gen | Heat Input | Heat Rate | Factor | Total Cost | Rate | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh |  | $/MWH | $/Hr | Btu/Kwh |  | $/MWH
0 | 578.23
70 | 879.104 | 12558.6286 | 1 | 52.3106 | 3661.7443 | 4298.2 |  | 18.6081 | 18.6081
90 | 1054.708 | 11718.9778 | 1 | 48.6468 | 4378.2086 | 8780.2 |  | 35.8232 | 35.8232
100 | 1157.45 | 11574.5 | 4 | 50.224 | 5022.396 | 10274.2 |  | 64.4187 | 64.4187

## 1 on 1 CC Heat Rate Curves
Minimum Load
Base Load
Peak Load
Fuel Cost = $4 mmBtu
VOM = $75/EOH
No Load Cost = No Load Fuel x Fuel Cost
= $ 2,359/hr

## 1 on 1 CC Heat Input
Fitted Regression Line Equation
No Load Fuel = 578.23 mmBtu/hr
Minimum Load
Base Load
Peak Load

## CC 1 on 1
Combined Cycle - 1 on 1
Heat Rate Curves
Output | Heat Input | Heat Rate | Incrementals
(MW) | (MBtu/hr) | (Btu/kWh) | (Btu/kWh)
0 | 578.23 |  |  | No Load
105 | 879.02 | 8371.619 | 2864.6667 | Min
135 | 1054.57 | 7811.6296 | 5851.6667 | Base
150 | 1157.28 | 7715.2 | 6847.3333 | Peak
Conditions at 59F
a= | 578.23 | (No Load Fuel) |  |  |  | Fuel Cost | 4 | $/mmBtu
b= | 0.5414 |  |  |  |  | VOM | 75 | $/EOH
c= | 0.0221 |  |  |  |  | PF | 1.02
Gas |  |  | Maintenance |  | Operating | Incremental | No Load = | 2359.1784
Net Gen | Heat Input | Heat Rate | Factor | Total Cost | Rate | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh |  | $/MWH | $/Hr | Btu/Kwh |  | $/MWH
0 | 578.23
105 | 878.7295 | 8368.8524 | 1 | 34.8592 | 3660.2164 | 2861.9 |  | 12.3908 | 12.3908
135 | 1054.0915 | 7808.0852 | 1 | 32.4125 | 4375.6933 | 5845.4 |  | 23.8492 | 23.8492
150 | 1156.69 | 7711.2667 | 4 | 33.462 | 5019.2952 | 6839.9 |  | 42.9068 | 42.9068

## CC PF Heat Rate Curves
Fuel Cost - $4/mmBtu
VOM Cost - $75/EOH
1 CT at Minimum
1 CT at Base
2 CT at Base
2 CT at Peak
No Load Cost = No Load Fuel x Fuel Cost
= $ 700/hr

## CC PF Heat Input
Fitted Regression Line Equation
No Load Fuel = 171.56 mmBtu/hr
1 CT at Minimum
1 CT at Base
2 CT at Base
2 CT at Peak

## CC 2 on 1 PF
2 on 1 Combined Cycle Heat Rate & Cost Curves
Output | Heat Input | Heat Rate | Incrementals
(MW) | (MBtu/hr) | (Btu/kWh) | (Btu/kWh)
0 | 578.23 |  |  | No Load
105 | 879.02 | 8371.619 | 2864.6667 | Min 1 CT
135 | 1054.57 | 7811.6296 | 5851.6667 | Base 1 CT
270 | 2109.14 | 7811.6296 | 7811.6296 | Base 2 CT
300 | 2314.56 | 7715.2 | 6847.3333 | Peak 2 CT
Conditions at 59F
a= | 171.56 | (No Load Fuel) |  |  |  | Fuel Cost | 4 | $/mmBtu
b= | 6.2856 |  |  |  |  | VOM | 75 | $/EOH
c= | 0.003 |  |  |  |  | PF | 1.02
Gas |  |  | Maintenance |  | Operating | Incremental | No Load = | 699.9648
Net Gen | Heat Input | Heat Rate | Factor | Total Cost | Rate | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh |  | $/MWH | $/Hr | Btu/Kwh |  | $/MWH
0 | 171.56
105 | 864.623 | 8234.5048 | 1 | 34.3111 | 3602.6618 | 6600.6 |  | 27.6447 | 27.6447
135 | 1074.791 | 7961.4148 | 1 | 33.0381 | 4460.1473 | 7005.6 |  | 28.5828 | 28.5828
270 | 2087.372 | 7731.0074 | 2 | 32.0981 | 8666.4778 | 7500.6 |  | 31.158 | 31.158
300 | 2327.24 | 7757.4667 | 8 | 33.6505 | 10095.1392 | 7590.6 |  | 34.1515 | 34.1515

## CC DB Heat Rate Curves
Fuel Cost - $4/mmBtu
VOM Cost - $75/EOH
1 CT at Minimum
1 CT at Base
2 CT at Base
2 CT with DB
No Load Cost = No Load Fuel x Fuel Cost
= $ 1,274/hr

## CC DB Heat Input
Fitted Regression Line Equation
No Load Fuel = 312.36 mmBtu/hr
1 CT at Minimum
1 CT at Base
2 CT at Base
2 CT with DB

## CC 2 on 1 DB
2 on 1 Combined Cycle Heat Rate & Cost Curves
Output | Heat Input | Heat Rate | Incrementals
(MW) | (MBtu/hr) | (Btu/kWh) | (Btu/kWh)
0 | 578.23 |  |  | No Load
105 | 879.02 | 8371.619 | 2864.6667 | Min 1 CT
135 | 1054.57 | 7811.6296 | 5851.6667 | Base 1 CT
270 | 2109.14 | 7811.6296 | 7811.6296 | Base 2 CT
300 | 2361.81 | 7872.7 | 8422.3333 | Duct Burner On
Conditions at 59F
a= | 312.36 | (No Load Fuel) |  |  |  | Fuel Cost | 4 | $/mmBtu
b= | 4.5164 |  |  |  |  | VOM | 75 | $/EOH
c= | 0.0078 |  |  |  |  | PF | 1.02
Gas |  |  | Maintenance |  | Operating | Incremental | No Load = | 1274.4288
Net Gen | Heat Input | Heat Rate | Factor | Total Cost | Rate | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh |  | $/MWH | $/Hr | Btu/Kwh |  | $/MWH
0 | 312.36
105 | 872.577 | 8310.2571 | 1 | 34.6201 | 3635.1142 | 5335.4 |  | 22.4827 | 22.4827
135 | 1064.229 | 7883.1778 | 1 | 32.7189 | 4417.0543 | 6388.4 |  | 26.0647 | 26.0647
270 | 2100.408 | 7779.2889 | 2 | 32.2951 | 8719.6646 | 7675.4 |  | 31.8712 | 31.8712
300 | 2369.28 | 7897.6 | 2 | 32.7222 | 9816.6624 | 7909.4 |  | 32.7249 | 32.7249

## CC EC Heat Rate Curves
Fuel Cost - $4/mmBtu
VOM Cost - $75/EOH
1 CT at Minimum
1 CT at Base
2 CT at Base
2 CT with Evap Coolers
No Load Cost = No Load Fuel x Fuel Cost
= $ 1,081/hr

## CC EC Heat Input
Fitted Regression Line Equation
No Load Fuel = 265.05 mmBtu/hr
1 CT at Minimum
1 CT at Base
2 CT at Base
2 CT with Evap Cooler

## CC 2 on 1 EC
2 on 1 Combined Cycle Heat Rate & Cost Curves
Output | Heat Input | Heat Rate | Incrementals
(MW) | (MBtu/hr) | (Btu/kWh) | (Btu/kWh)
0 | 578.23 |  |  | No Load
105 | 879.02 | 8371.619 | 2864.6667 | Min 1 CT
135 | 1054.57 | 7811.6296 | 5851.6667 | Base 1 CT
270 | 2109.14 | 7811.6296 | 7811.6296 | Base 2 CT
284 | 2181.94 | 7682.8873 | 5200 | Evap Cooler On
Conditions at 59F
a= | 265.05 | (No Load Fuel) |  |  |  | Fuel Cost | 4 | $/mmBtu
b= | 5.1453 |  |  |  |  | VOM | 75 | $/EOH
c= | 0.0059 |  |  |  |  | PF | 1.02
Gas |  |  | Maintenance |  | Operating | Incremental | No Load = | 1081.404
Net Gen | Heat Input | Heat Rate | Factor | Total Cost | Rate | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh |  | $/MWH | $/Hr | Btu/Kwh |  | $/MWH
0 | 265.05
105 | 870.354 | 8289.0857 | 1 | 34.5338 | 3626.0443 | 5764.8 |  | 24.2347 | 24.2347
135 | 1067.193 | 7905.1333 | 1 | 32.8085 | 4429.1474 | 6561.3 |  | 26.7701 | 26.7701
270 | 2084.391 | 7719.9667 | 2 | 32.053 | 8654.3153 | 7534.8 |  | 31.2975 | 31.2975
284 | 2202.1856 | 7754.1746 | 2 | 32.1652 | 9134.9172 | 7617.4 |  | 31.5823 | 31.5823