## Setup
Enter Stakeholder Group Name in cell A2:
[GroupName]
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
[IssueTitle]

## 1. Interest Identification
PFRSTF
Primary Frequency Response Sr. Task Force
Interest Identification
Instructions: List interests of all parties on this page.
1 | Ensure adequate Primary Frequency Response during system restoration events.
2 | Ensure no degradation to BAL-003-1 performance considering the changing resource mix.
3 | Enable greater predictability and consistency of system Primary Frequency Response.
4 | Increase confidence level in generator frequency response settings including a better understanding of current generation operating modes and their impact on frequency response.
5 | Minimize generator financial impacts (i.e. headroom requirments).
6 | Implement a solution consistent with regulatory compliance and guidance (FERC/NERC)
7 | Solution should be resource-type neutral where possible.
8 | Ensure market rules won't discourage resources from providing Primary Frequency Response (i.e. 5 min settlement deviation, regulation scoring, capacity performance, performance assessment hour)
9 | Development of an apples to apples comparison to facilitate a standardized product definition. Quantify what PFR is worth.
10 | Develop a solution for the transition and coordination from primary to secondary response.
11 | Primary frequency response is bi-directional product. Capability is expected in both directions.
12 | Proactively plan for potential future requirements.
13 | Modifying the synchronized reserve to include a frequency component.
14 | Ensuring enough primary frequency response is available at all times to recover from larger system disturbances.
15 | Ensuring costs are adequately covered and compensation is covered.
16 | Visibility of frequency response to real time operators.
17 | Ensure energy storage resources are not unfairly impacted by PJM's requirements.
18 | Include an exemption process and criteria for technical or operational considerations.
19 | Tie any requirements for PFR directly to compensation
20 | Carefully consider the implications of creating a frequency response performance evaluation

## 2. Options Matrix- Design Comp.
PFRSTF
Primary Frequency Response Sr. Task Force
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E | F | G | H
1 | Interconnection PFR Requirement | High | Balancing Authority Requirement BAL-003-1 FRO = 258.63 MW/.1 Hz for 2017
| Individual Unit Requirement | High | New units PFR requirement is in Interconnection Service Agreement | Supplemental additional freq response for more significant events | Individual unit capability requirement for PFR | Individual unit capability requirement for PFR by resource class | Include appropriate requiremetns for energy storage resources regarding sustained response | Determine individual unit MW obligation for every resource type (no exceptions)
1a | Droop Setting | High | Not to exceed 5% (M-14D) | A: Different droop setting by resource class
1b | Deadband | High | Not to exceed +/- 36 mHz (M-14D) | A: Move to +/- 17 mHz; B: Maintain consistency with Eastern Interconnection
1c | Plant level Digital Control Systems (i.e. outerloop controls) | Low - High | Undefined | Utilize locally sensed frequency as input in control system | Digital control systems must allow unit to provide PFR | Digital control systems should if posible allow unit to provide PFR | For Blackstart or critical load units utilize locally sensed frequency as input | Control of generator output should incorporate a bias for frequency error to allow governor action. Other runbacks and overides may be used as needed to protect the generating equipment.
1d | Governor Equivalent Mode of Operation (i.e. MW setpoint) | Low - High | Unrestricted governor control (M14-D, Sec 7.1.1) | Utilize locally sensed frequency as input in control system | Governor equivalent mode of operation must allow unit to provide PFR | Governor equivalent mode of operation should if possible allow unit to provide PFR | For Blackstart or critical load units utilize locally sensed frequency as input | Include appropriate requirements for energy storage devices | The phrase from Man. 14-D "equivalent electronic speed control device" should be changed to "electronic load/frequency controller" to account for inverter based generation
1e | "Headroom/Footroom" requirement | Low | None
1f | Bi-directional Frequency Response | Low | Undefined | A: Additional manual language clarifying bi-directional requirement
1g | Automatic detection and response to local frequency measures | Low - High | M-14D | A: Additional clarifying manual language; B: Local frequency or speed measurements and autonomous control are necessary
2 | Required Resources | High | Nameplate > 75 MVA (aggregated) | Clarification of definition of aggregated resource | Apply to all smal and large, new and existing resources | Optional for all resources | Apply to all new generator interconnection (> 20 MVA; consistent with voltage schedule) and existing units > 75 MVA or consistent with FERC NOPR | Aggregation behind the POI for all generating resources | Determine individual unit MW obligation for every resource type (no exceptions)
2a | New/Existing resources | High | All resources (new and existing) with exception process (M-14D) | A: Optional for all resources; B: Required for new resources only; C: Required for all resources; D: Required for all new and existing resources (Existing units > 75 MVA)
2b | Exempt Resources | High | Nuclear generation | Resources with low capacity factors | Units greater than 25 years old | Documented exception process similar to PLS | Acquiring replacement obligation if not providing service | Need exemption process and criteria for technical or operational considerations. | None
3 | Inertial response | Low - Medium | No requirements for any resources | A: Differentiate between intertial response from govenor frequency control
4 | Performance requirement/verification | High | "System" response measured for compliance with BAL-003-1. No individual unit performance requirements. MOD-27 requirements | A: Measured individual unit performance during selected frequency events; B: Penalties for non-performance; C: Reserve right to report non-performance to FERC; D: Frequency excursions outside the 36 mHz deadband limits are rare iin the EI. Frequency excursions above 60.060 or below 59.940 would be necessary to fairly evaluate performance
5 | Compensation mechanism | High | None (included in offer) | Payment based on MW response times LMP multiplier | Opportunity cost payment if headroom is maintained to provide frequency response | Recovery through capacity market through CONE | Cost of Service structure (filed with FERC similar to Sched 2) | Market based product, similar to Regulation | Capital investment is already included in CONE. VOM is included in the CP offer. | Explore compensation for synchronous intertial capability | Develop secondary market to allow resources that can't or choose not to meet obligation to purchase PFR from othe resources. | Low
6 | Telemetry requirements | High | Manual M-01 requirements (10 seconds) | A: 2 sec. scan rate for performance assessment; B: 2 sec. scan rate on new generators; C: Generator output measurement and transmission resolution should be at least 0.1 MW or 1% (whichever is less)
7 | Additional requirements for Blackstart or Critical Load units | High | Blackstart must be capable of isochronous control (maintain voltage and frequency under varying loads (m-36) Yearly Blackstart unit testing | A: Clarify "under varying load" terminology in M-36 for Blackstart units; B: Clarify mode of operation for governor equivalent; C: For Blackstart or critical load units utilize locally sensed frequency as input | Low - Medium
8 | Treatment of regulating units | Medium | Not defined | A: Expected to provide PFR; B: Not expected to provide PFR; C: Expected to provide PFR, no impact to regulation score; D: Not expected to provide PFR during hours unit is assigned regulation
9 | Treatment of pseudo tied or dynamically scheduled units | Medium | Not defined | Pseudo-tied expected to provide PFR | Pseudo-tied not expected to provide PFR | Dynamically scheduled units expected to provide PFR | Dynamically scheduled units not expected to provide PFR | Dynamically scheduled units follow rules of native BA
10 | Treatment of units providing synchronized reserve | Medium | Not defined | A: Expected to provide PFR; B: Not expected to provide PFR; C: Expected to provide PFR, no impact to sync reserve score
11 | Treatment of CP units in Performance Assessment Hour | Medium | Not defined | A: Providing PFR should not result in PAH penalty; B: Pro-ration of frequency response service should be reflected in PAH calculation (penalty/bonus); C: Frequency response not included in PAI calculation. | Low - High
12 | Treatment of DER resources | Medium | Not defined | A: Wholesale DER would meet all frequency requirements; B: Interconnection agreement vs. WMPA | Medium
13 | Treatment of intertial synchronous motors load providing frequency response | Medium | Not defined
14 | Allowing load based frequency response service/product | Low | Not defined | A: Limit the LR capacity to % of the minimum generating reserve
15 | Implemenation Plan | High | [9 empty] | Medium - High
16 | Evaluate benefits of different resource types. Benefits factor | High | Not defined | [8 empty] | High
PJM Additions
ESA Additions
AEP Additions
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attibute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
PFRSTF
Primary Frequency Response Sr. Task Force
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
PFRSTF
Primary Frequency Response Sr. Task Force
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
2B Documented Exception Process | Nuclear. Targeted exception process for existing resources which might be different from new resources. Not allowing exceptions for units needed in restoration process. Units scheduled to retire that may require capital investment.
4 Resource Performance Measurement | Units providing regulation will not have their regulation performance score impacted. High level correct direction response. Factor in physical limitations of a unit. Telemetry failure. BAL/TRE requirement.
5 Compensation Mechanism
11 PAH hour determination
12 Treatment of DER | If interconnection service agreement is signed then PFR is required. If participating in PJM markets, then must provide PFR.

## 3. Package Matrix
PFRSTF
Primary Frequency Response Sr. Task Force
PACKAGE/ PROPOSAL MATRIX
Instructions:
1. Copy over design component, priority, and status quo columns from options matrix
2. Complete individual packages in columns by selecting individual component options from the options matrix.
Packages
# | Design Components | Priority | Status Quo | PJM | IMM | C-Power | AEP - A | AEP - A'
1 | Frequency Response Requirement | High | Balancing Authority Requirement BAL-003-1 FRO = 258.63 MW/.1 Hz for 2017 | Individual unit capability requirement for PFR | Same as PJM | Same as PJM | Same as PJM | Same as PJM
1a | Droop Setting | High | Not to exceed 5% (M-14D) | Status Quo | Same as PJM | Same as PJM | Same as PJM | Same as PJM
1b | Deadband | High | Not to exceed +/- 36 mHz (M-14D) | Status Quo but maintain consistency with Eastern Interconnection | Same as PJM | Same as PJM | Same as PJM | Same as PJM
1c | Plant level Digital Control Systems (i.e. outerloop controls) | Low - High | Undefined | Utilize locally sensed frequency as input in control system; Digital control systems must allow unit to provide PFR | Same as PJM | Same as PJM | Utilize locally sensed frequency as input in control system to correct unit output demand for frequency error. This should reflect the governor deadband and droop sttings. | Utilize locally sensed frequency as input in control system to correct unit output demand for frequency error. This should reflect the governor deadband and droop sttings.
1d | Governor Equivalent Mode of Operation (i.e. MW setpoint) | Low - High | Unrestricted governor control (M14-D, Sec 7.1.1) | Utilize locally sensed frequency as input in control system; Governor equivalent mode of operation must allow unit to provide PFR | Same as PJM | Same as PJM | Same as PJM | Same as PJM
1e | "Headroom/Footroom" requirement | Low | None | Status Quo | Same as PJM | Same as PJM | Units operating above 95% Eco Max or below 5% Eco Min should be exempted from performance assessment. | Units operating above 95% Eco Max or below 5% Eco Min should be exempted from performance assessment.
1f | Bi-directional Frequency Response | Low | Undefined | Additional manual language (M14D) clarifying bi-directional requirement | Same as PJM | Same as PJM | Same as PJM
1g | Automatic detection and response to local frequency measures | Low - High | M-14D | Additional clarifying manual language (M14D) | Same as PJM | Same as PJM | Same as PJM
2 | Required Resources | High | Nameplate > 75 MVA (aggregated) | Apply to all small and large, new and existing resources. | Same as PJM | Nameplate>20MW | Same as PJM | Same as PJM | Low
2a | New/Existing resources | High | All resources (new and existing) with exception process (M-14D) | Required for all resources | Same as PJM | Same as PJM | Same as PJM | Same as PJM | Low - Medium
2b | Exempt Resources | High | Nuclear generation | Nuclear units exempt; documented exception process. Existing resources <10 MW exempt. | Same as PJM | Nuclear units exempt; documented exception process , Resources less than 20MW. | Nuclear units and existing units requiring reconfigurations. Resources that sought recovery of costs but were denied by the FERC. Partial exemptions for mechanical governor equipment limitations. | Nuclear units and existing units requiring reconfigurations. Resources that sought recovery of costs but were denied by the FERC. Partial exemptions for mechanical governor equipment limitations. | Low - High
3 | Inertial response | Low - Medium | No requirements for any resources | Status Quo | Same as PJM | Same as PJM | Inverter-based Resources are exempt from providing synchronous inertial response;PJM to study the value of synchronous intertial response in restoration, including the substitution rate of assets providing synchronous inertia to that of resources that cannot provide synchronous inertia. PJM to report by 6/1/20. | Inverter-based Resources are exempt from providing synchronous inertial response;PJM to study the value of synchronous intertial response in restoration, including the substitution rate of assets providing synchronous inertia to that of resources that cannot provide synchronous inertia. PJM to report by 6/1/20. | Medium
4 | Performance requirement/verification | High | "System" response measured for compliance with BAL-003-1. No individual unit performance requirements. MOD-27 requirements | Measured individual unit performance during selected frequency events; PJM reserves right to report non-performance to FERC | Same as PJM | Same as PJM | Measured individual unit performance during selected frequency events for units receiving cost recovery from FERC. PJM reserves right to report non-performance of these assets to FERC. Units that filed for compensation at FERC, but were denied, shall have no performance obligation. Compliance with a performance obligation shall be judged on the basis of the average of the last five evaluations. Success is a 50% or greater per unit response.The criteria for determining an event is used for performance evaluations shall be published. | Measured individual unit performance during selected frequency events for units receiving cost recovery from FERC. PJM reserves right to report non-performance of these assets to FERC. Units that filed for compensation at FERC, but were denied, shall have no performance obligation. Compliance with a performance obligation shall be judged on the basis of the average of the last five evaluations. Success is a 50% or greater per unit response..The criteria for determining an event is used for performance evaluations shall be published. | Medium - High
5 | Compensation mechanism | High | None (included in offer) | Cost of Service structure filed with FERC (similar to Reactive Schedule 2) for existing resources (resources with signed ISA or WMPA at time requirements become effective) | Capital investment is already included in CONE. VOM is included in the CP offer. | Same as PJM | Same as PJM plus can include anticipated lost opportunity costs due to inefficiencies of design changes due to control modifications to provide PFR with the Cost of Service Structure ; or until complications related to market products are overcome | Same as PJM plus can include anticipated lost opportunity costs due to inefficiencies of design changes due to control modifications to provide PFR with the Cost of Service Structure ; or until complications related to market products are overcome | High
6 | Telemetry requirements | High | Manual M-01 requirements (10 seconds) | Move to 2 second scan rate for new generators | Same as PJM | Same as PJM | Same as PJM | Same as PJM
7 | Additional requirements for Blackstart or Critical Load units | High | Blackstart must be capable of isochronous control (maintain voltage and frequency under varying loads (m-36) Yearly Blackstart unit testing | Status Quo | Same as PJM | Same as PJM | Same as PJM | Same as PJM
8 | Treatment of regulating units | Medium | Not defined | No performance assessment for PFR during hours unit is assigned regulation. No adjustment for regulation performance score. | Same as PJM | Same as PJM | Same as PJM | Same as PJM
9 | Treatment of pseudo tied or dynamically scheduled units | Medium | Not defined | Pseudo-tied resources must meet requirements above. Dynamically scheduled units follow rules of native BA. | Same as PJM | Same as PJM | Same as PJM | Same as PJM
10 | Treatment of units providing synchronized reserve | Medium | Not defined | Expected to provide PFR | Same as PJM | Same as PJM | Same as PJM | Same as PJM
11 | Treatment of CP units in Performance Assessment Interval | Medium | Not defined | PFR response would be accounted for in the Expected MW calculation during PAI | Same as PJM | Same as PJM | Same as PJM | Same as PJM
12 | Treatment of DER resources | Medium | Not defined | Wholesale DER subject to PFR requirements; Requirements to be documented in M-14D. For new resources, requirements apply to resources with ISA or WMPA. | Same as PJM | Same as PJM | Same as PJM | Same as PJM
13 | Treatment of load resources providing frequency response | Medium | Not defined | Status Quo | Same as PJM | Same as PJM | Load response providing frequency response shall have same requirements of a generator; including access to compensation mechanisms | Same as PJM
14 | Implemenation Plan | High |  | 24 months from approved Manual requirements. Exception process for resources needing longer time to implement. PJM staff will provide quarterly updates to Operating Committee on PFR performance and trends. PJM staff will continue to follow industry and regulatory developments in PFR. PJM staff will consider PFR issues during restoration planning of the Black Start RFP. PFRSTF will go on hiatus for 9-12 months. PFRSTF will reconvene in the Fall/Winter of 2018 to review current status and discuss next steps. | Same as PJM | Same as PJM | New resources in PJM que after 12/31/18 must have necessary equipment to provide service upon commercial operation. Existing resources, including those in the que prior to 1/1/19, requiring modifications are to be completed by 6/1/21, unless an alternative date is agreed upon. | New resources in PJM que after 12/31/18 must have necessary equipment to provide service upon commercial operation. Existing resources, including those in the que prior to 1/1/19, requiring modifications are to be completed by 6/1/21, unless an alternative date is agreed upon.
15 | Evaluate benefits of different resource types. Benefits factor | High | Not defined | Status Quo | Same as PJM | Same as PJM | Same as PJM | Same as PJM
16 | Treatment of imbalance and operating reserve charges for units following basepoints for energy | High | PJM does not take into account the impact of following frequency for computation of energy imbalance and operating reserves |  |  |  | PJM shall compute a default value of theoretic response given the online portfolio of resources responding to PFR. PJM increase or decrease the billing settlement related basepoint by this amount. | Status Quo

## 3a. Package Details
PFRSTF
Primary Frequency Response Sr. Task Force
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
PFRSTF
Primary Frequency Response Sr. Task Force
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
PFRSTF
Primary Frequency Response Sr. Task Force
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3