## RASTF Analysis Requests
| Data and Analysis | Contributor | Contributed Date | Related Key Work Activities | Level of difficulty to complete the request populated by PJM/IMM staff | Status | Expected Date | Reference
1 | Conduct full expansion of Astrapé analysis to RTO level Astrapé observed that, unlike existing ELCC accreditation, thermal accreditation today is based on average outage rates and therefore does not account for outage variability or correlations. Astrapé shows that outages vary significantly during times of system tightness from expected average outages and necessitate more reserves than are assessed under the EFORd approach used today. Astrapé developed a methodology focusing on four areas of risk to isolate the impacts of variability and important correlations and thereby accredit thermal resources on a more accurate basis. a. What would be the outcome of applying this methodology to PJM’s full thermal fleet across the RTO, rather than just PJM South and filling in gaps where Astrapé used public estimated data with PJM actual and up-to-date data? Requested PJM Analysis: Undertake complete analysis described above. | AEE | 2022-06-15 | KWA 2; KWA 5 | High | Partially complete (analysis under status quo assumptions was provided; full analysis can only be performed when a decision has been made about how to model each of the thermal inputs) | TBD | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220808/item-04---thermal-outages-data-analysis.ashx
2 | Review of Outage Variability As one of four areas of risk, Astrapé identified that thermal accreditation today does not account for the variability in outages and pursuant reserve requirements that are needed to account for general variability/correlations. This is accounted for in existing renewable/storage ELCC metrics. a. What are the outcomes using the Astrapé methodology to assess Outage Variability de-rate on thermal resources on an RTO level? b. Given that the demand side now accounts for variability in outages, how would this change once outage variability is accounted for on the supply side? Requested PJM Analysis: 1. Perform outage variability analysis per the Astrapé paper methodology pages 27-30. 2. Evaluate changes to how demand side accounts for variability in outages. | AEE | 2022-06-15 | KWA 2; KWA 5 | Low | Complete |  | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220808/item-04---thermal-outages-data-analysis.ashx
3 | Review of Correlated Hot and Cold Weather Dependent Outages of Unlimited Resources Astrapé used Sinnott Murphy’s findings on correlation between weather and forced outages to develop a weather-dependent de-rate factor by generation type. Single classes for generation types are broad and may not capture important intra-class distinctions. Can PJM assess the prudency of further intra-class distinctions and undertake related analysis of resource adequacy characteristics, including considering the impact of generator size, different technologies, and other salient criteria that can contribute to resource adequacy contributions and should be considered in informing possible subclasses? Requested PJM Analysis: 1. Run statistics (average, 95% range) to determine the correlation between temperature and EFOR at specific temperature thresholds. a. Run this on EFOR as well, which only captures unit outages and not derates. This gives a clearer picture of binary performance vs. ambient derates. b. Perform statistical analysis comparing the distribution of system outages using uncorrelated random sampling to the historical distribution of system outages. 2. Provide this data in aggregate and under buckets related to unit size, unit age, etc. 3. Run analysis with and without controlling for fuel availability. | AEE | 2022-06-15 | KWA 2; KWA 5 | Medium | Complete | August and Sept 2022 RASTF | 1. https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220808/item-04---thermal-outages-data-analysis.ashx 2. https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220922/item-02---rastf-data-analysis---september-2022.ashx
4 | Review of Fuel Availability Outages of Unlimited Resources Astrapé highlighted recent experiences that suggest under emergencies, ~10% of the gas fleet cannot obtain fuel. This raises questions such as whether and how units can effectively mitigate this risk partially (for instance, by obtaining firm fuel) or in whole? a. What is the scale and correlations of fuel related outages over the last 10 years in PJM? b. What portion of gas generation would be expected now or in the future to have fuel under specific weather events/temperatures due to constraints in gas delivery infrastructure? c. Is there a distinction in outage profiles between resources that have firm and non-firm fuel contracts? d. Is there a distinction in outage profiles between resources that have on-site fuel back up and do not? e. Is there a distinction in outage profiles dependent on where the generation resource is located on the gas distribution system (such as behind an LDC), or on a main transmission pipeline lateral)? f. Is there a distinction between resources that have DA energy schedules and are able to commit to timely gas day ahead nomination timelines and resources that are committed in the real time and may only nominate their gas intraday? Requested PJM Analysis: 1. Run statistics (average, 95% range) to determine the correlation between fuel and EFOR at specific temperature thresholds. a. Perform statistical analysis comparing the distribution of system outages using uncorrelated random sampling to the historical distribution of system outages. 2. Provide this data in aggregate and under buckets related to unit size, unit age, etc. a. The specific GADS cause codes related to fuel supply issues: • 9130: “failure of fuel supplier to fulfill contractual obligations…due to physical fuel disruptions or operational impairments…” • 9131: “lack of fuel – due to contractual or tariff provisions that allow for service interruption…” • 9134: “fuel conservation” | AEE | 2022-06-15 | KWA 2; KWA 5 | Medium | Complete | August and Sept 2022 RASTF | 1. https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220808/item-04---thermal-outages-data-analysis.ashx 2. https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220922/item-02---rastf-data-analysis---september-2022.ashx
5 | Review of Common Mode Failure of Unlimited Resources Astrapé highlighted in its paper that some units share transformers and other facilities that can lead to correlated outages not accounted for today. a. What is the frequency of common mode failure? b. What are the trends over the last 10 years Requested PJM Analysis: Analyze the frequency of common mode failures by using GADS data and running a query of the same time period and cause code. This will assess the incidence of common mode failure | AEE | 2022-06-15 | KWA 2; KWA 5 | High | Partially complete (some initial conclusions of analysis were presented on 08/08/2021) | Oct 2022 RASTF | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220808/item-04---thermal-outages-data-analysis.ashx
6 | Review of Maintenance Outages of Unlimited Thermal Resources PJM explained in its analysis that PJM procures about 1,500 MW in the RRS to account for these. “The RRS, CETO, ELCC use most recent 5-year Equivalent Maintenance Outage Factor (EMOF) calculated using GADS data. A quarter (1/4) of the EMOF is added to the EFORd to create the EFORd of each unit; the remainder (3/4) is added to the EPOF” (KWA 2 Matrix) a. How is this 1,500 MW calculated? b. How is it shared across the PJM fleet? Is a single resource type responsible for it? c. Is there a specific time period of maintenance outages that is responsible for requiring this 1,500 MW? Requested PJM Analysis: 1. Analyze maintenance outages by month, resource type, and contribution to the RRS. 2. Investigate how and if maintenance outages reduce system reliability at all due to approval of multiple outages during periods that unexpectedly see higher system stress (demand/forced outages) than expected. a. For instance, in ERCOT there have been reports in May that planned outages are requested and approved for large amounts of thermal resources during the same periods which then see higher demand than expected, thus creating system stress events 3. Additional PJM analysis to fully analyze the study questions. | AEE | 2022-06-15 | KWA 2; KWA 5 | Medium | Complete | Oct 2022 RASTF | 1. https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220808/item-04---thermal-outages-data-analysis.ashx 2. https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221031/item-03----rastf-data-analysis---october-2022.ashx
7 | Review of Ambient Derates of Unlimited Thermal Resource PJM in its analysis identified 2,500 MW in RRS that must be procured due to ambient derates. a. How does this 2,500 MW figure get calculated and how does it interact with the ICAP calculation? b. How are these 2,500 MW distributed by resource type? c. On a unit level, what is the appropriate additional de-rate to EFORd to account for ambient derates? d. Since ambient de-rates presumably occur during periods of system stress and are correlated across the system, has analysis been performed to quantify the impact on thermal resources’ capacity contribution? Requested PJM Analysis: Analyze ambient derates to fully analyze the study questions. | AEE | 2022-06-15 | KWA 2; KWA 5 | Medium | Complete |  | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220808/item-04---thermal-outages-data-analysis.ashx
8 | Review Planned Outages of Unlimited Thermal Resources 1. For ELCC resources, planned outages are part of their accreditation, while for Unlimited Thermal Resources, planned outages do not contribute to accreditation. PJM explained in its December analysis that the impact today on the RTO reliability requirement is currently 0 MW UCAP, but the impact on the reliability requirement of modeled LDAs that have risk spread-out across seasons is greater than 0. Concepts such as Equivalent Availability Factor aim to account for Planned Outages in Accreditation, something that the IMM has highlighted, in particular. a. What is the impact of Planned Outages on the RRS within modelled LDAs today and how does that affect overall capacity procurement by affecting CETO etc.? b. What is the impact of Planned Outages in the future based on expected changes in supply mix/demand across the RTO and within LDAs? c. Please share descriptive statistics on Planned Outages in the PJM fleet in terms of average duration, frequency, seasonality, and overall quantity by asset type, asset age, etc. Requested PJM Analysis: Analyze Planned Outages fully to analyze the study questions. | AEE | 2022-06-15 | KWA 2; KWA 5 | Medium | Complete | Oct 2022 RASTF | 1. https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220808/item-04---thermal-outages-data-analysis.ashx 2. https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221031/item-03----rastf-data-analysis---october-2022.ashx
9 | For May and June hot weather events, what were the outputs of Variable Resources in real time versus their accreditation by hour? Same for thermal, but in terms of availability to account for dispatch decision. | Roy Shanker | 2022-08-08 | KWA 5 | Low | Complete | Sept 2022 RASTF | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220922/item-02---rastf-data-analysis---september-2022.ashx
10 | Typical MW of planned maintenance by week of year, recent years. A. Maybe a qualitative discussion of how the pattern of weekly planned outage has changed in recent years and may further change as the resource mix changes. | Jim Wilson, consultant to the consumer advocates of NJ, PA, MD, DC, DE | 2022-08-25 | KWA 2; KWA 3; KWA 8 | Low | Complete | Oct 2022 RASTF | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221031/item-03----rastf-data-analysis---october-2022.ashx
11 | PJM’s estimates of the weekly “headroom” or “generator outage margin” (see OC presentation linked below) available for planned outage scheduling. a. Comparison of the headroom available to the recent pattern of actual planned maintenance, showing in which weeks the headroom was nearly fully used, etc. https://www.pjm.com/-/media/committees-groups/committees/oc/2022/20220819-special/item-02---education---generator-outage-scheduling-overview---20220819.ashx | Jim Wilson, consultant to the consumer advocates of NJ, PA, MD, DC, DE | 2022-08-25 | KWA 2; KWA 3; KWA 8 | Low | Complete | Nov 2022 RASTF | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221110/item-03---rastf-data-analysis---november-2022.ashx
12 | Estimates of the headroom or generator outage margin that would be available by week under a 3- or 4-season seasonal capacity market construct. You would have to make some assumptions about how the seasons are defined, and how the reliability requirement would be determined for each season. Any reasonable assumptions could be used for this educational exercise. a. Comparison of this pattern of headroom to recent and anticipated future planned outage needs. Some planned maintenance would likely have to shift. Do things get tight overall, or only in some additional weeks of the year? | Jim Wilson, consultant to the consumer advocates of NJ, PA, MD, DC, DE | 2022-08-25 | KWA 2; KWA 3; KWA 8 | Medium | Partially Complete (clarification on request during initital presentation may yield additional information to present) | Nov 2022 RASTF | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221130/item-3---rastf-data-analysis---november-2022.ashx
13 | Add additional data to information presented at the Sept 2022 RASTF (https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20220922/item-02---rastf-data-analysis---september-2022.ashx) - Study pre and post Capacity Performance and fleets by year (to capture retirements) - Use actual temperature rather than average temperature - Show coal as a percentage of ICAP and UCAP - Add peak outage to slide 12 - Add peak load to Saturday and Holiday Slide | Multiple Stakeholders | 2022-09-22 | KWA 2; KWA 5 | Medium | Partially Complete | TBD | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221011/rastf-data-analysis---october-2022.ashx
14 | Add additional data to the information presented at the October 2022 RASTF () -Use an example of a nuclear unit to better explain the Average PO MW Size x Duration by Year Slide -Look at cost codes in 2020 for coal -Run an analysis with planned retiredments removed for planned outages -Provide the NERC defintiion of planned versus maintenance outages -Look at the outages of units leading up to retirement, take into consideration age of unit -How successful are PJM and generation owners moving outages out of times when there is a need for reserves? Correlate with times of high prices. | Multiple Stakeholders (Joe Bowring, IMM, Jim Wilson, Consultant to the Consumer Advocates, Paul Sotkiewicz, E-Cubed Policy Associates, Mark Spencer. LS Power) | 2022-10-31 | KWA 2; KWA 3; KWA 8 | Medium | Partially Complete | Nov 2022 RASTF | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221110/item-03---rastf-data-analysis---november-2022.ashx
15 | Add additional data to the information presented at the November 2022 RASTF -Include 2022 data -Number of weeks on average coal units require for outages | Multiple Stakeholders (Jim Wilson, Consultant to the Consumer Advocates, Paul Sotkiewicz, E-Cubed Policy Associates) | 2022-11-10 | KWA 2; KWA 3; KWA 8 | Low | Complete | Nov 2022 RASTF | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221130/item-3---rastf-data-analysis---november-2022.ashx
16 | Present Planned Outage Data showing historical weekly peak load values | Mark Spencer, LS Power |  |  | Medium | Complete | Nov 2022 RASTF | https://www.pjm.com/-/media/committees-groups/task-forces/rastf/2022/20221130/item-3---rastf-data-analysis---november-2022.ashx
17
18
19
20

## Version
Version | Posting Date
1 | 8.26.2022
2 | 9.8.2022
3 | 10.06.2022
4 | 11.1.2022
5 | 11.22.2022
6 | 12.19.2022