## Setup
Enter Stakeholder Committee Name in cell A2:
Reactive Power Compensation Task Force
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Reactive Rate Process

## Buckets
Compensation | Process | Operational Topics
(3) Estimate of Current Cost method used by FERC | (5) Coordination of PJM OATT disposition and FPA Section 203 approved timelines | (9) PJM defined demand for reactive power
(4) Independent Rate Expert |  | (10) Required location on the grid
(6) Competitive Markets | (8) Transparency | (14) Enhancing PJM's Ability of maintaining reliability
(16) Reducing financial risk to PJM and Members | (11) Retain the reactive revenues achieved at FERC | (2) Analysis of Operational side of house (testing RP)
(19) Compensation for non-synchronous resources | (12) Simple process going forward | (28) Understanding the reliability impacts of voltage support on the distribution side of the transmission wholesale meter if distribution level resources are no longer required to provide reactive or cannot receive compensation for reactive in PJM
(20) Compensation for service rendered and control of the unit | (13) Predictability of Reactive Revenues for resources | (29) PJM's ability to fulfill its role as Reliability Coordinator if generation level no longer is required to comply with PJM directives because no compensation comes under Schedule 2
(21) Compensation tied to actual cost or well defined "Replacement costs" that can be easily verified | (15) Easing of Administrative burden (Settlements and Testing)
(22) Obligation implies compensation directly | (17) Reducing uncertainty and increasing transparency in rate design & operations
(23) Ensuring opportunity for generators to reasonably recover costs associated with reactive power capability | (18) Eligibility requirements
(24) Compensation design commensurate with other FERC defined AS (Black Start, Synch Reserve, Regulation, Non-Spin) based on the cost to have the option available and compensation for actual use if it requires cost | (26) Transition mechanisms for existing rates to new constructs that may be approved
(25) Compensation comparability based on MVAR output | (30) If distrubution connected resources are not eligible for Schedule 2 compensation, will PJM still require these resources obligations in existing FERC - accepted ISA requirements and in future ISA's
(27) Inclusion of ancillary services opportunity costs
(7) No double counting of reactive revenues

## 1. Interest Identification
Reactive Power Compensation Task Force
Reactive Rate Process
Interest Identification
Instructions: List interests of all parties on this page.
1 | Overview of the RPCTF issue
2 | Analysis of Operational side of house (Testing Reactive Power)
3 | Estimate of Current Cost method used by FERC
4 | Independent Rate Expert
5 | Coordination of PJM OATT disposition and FPA Section 203 approval timelines.
6 | Competitive Markets
7 | No Double Counting
8 | Transparency
9 | PJM defined demand for reactive
10 | Required location on the grid
11 | Retain the Reactive Revenues achieved at FERC
12 | Simplified process going forward
13 | Predictability of Reactive Revenues for Resources
14 | Enhancing PJM's Ability of maintaining reliability
15 | Easing of Administrative Burden (Settlements and Testing)
16 | Reducing Financial Risk to PJM and Members
17 | Reducing Uncertainty and Increasing Transparency in rate design and operations
18 | Eligibility Requirements
19 | Compensation for non-synchronous resources
20 | Compensation for service rendered and control of the unit
21 | Compensation tied to actual cost or well defined. "Replacement costs" that can be easily verified.
22 | Obligation implies compensation directly
23 | Ensuring opportunity for generators to reasonably recover costs associated with reactive power capability
24 | Compensation design commensurate with other FERC defined AS (i.e. Black start, synch reserve, regulation, non-spin) based on the cost to have the option available, and compensation for actual use if it requires costs
25 | Compensation comparability based on MVAR output
26 | Transition mechanisms for existing rates to new constructs that may be approved
27 | Inclusion of ancillary services opportunity costs
28 | Understanding the reliability impacts of voltage support on the distribution side of the transmission wholesale meter if distribution level resources are no longer required to provide reactive or cannot receive compensation for reactive in PJM

## 2. Options Matrix- Design Comp.
Reactive Power Compensation Task Force
Reactive Rate Process
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E | F | G | H | I | J
1 | Compensation Mechanism | High | Unit specific related/structured to the AEP methodology, FERC settlement proceedings, and filed rate. Payment via PJM Tariff Schedule 2- FERC Filed Rate | Unit-specific filed Rate | Flat Rate | Included in Capacity Payment | Flat rate by technology type | Capacity plus adjustment | Capability independent flat rate | A resource-specific, i.e., generator, cost of service filed at FERC using the AEP methodology | A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates preiodically, at least every three years.
1A | Basis for Compensation | High | FERC Approved Capability | MVAR Capability Nameplate | MVAR Capability ISA | MVAR Capability Tested | Delivered MVAR-h (useful to regulating voltage) | Regulation Capability (Target Voltage Regulation) | Tested MVAR capability beyond the ISA obligation | MW capability (ICAP or MFO, if applicable) | Tested and vaildated MVAR capability beyond the ISA obligation | Tested and validated MVAR capability | Streamlined AEP method. Two options: (A) unit-specific approach using AEP-based form; or (b) AEP-derived stated rate based on generation type
1B | Treatment of leading vs. lagging capabillity. Lagging means injecting |  |  | A: No different; B: Only lagging compensated; C: Different compensation for leading vs. lagging
1C | Eligibility for Compensation | High | FERC Determined | Located inside PJM footprint | Physically connected to PJM transmission facilities | Located in an area that benefits from reactive capability | Performs capability testing | Must have automatic voltage regulation operating at all times except for planned outaged. Requirement to be dispatched by PJM for reactive power as needed. | Must be modeled in PJM EMS and have all required telemetry | Any generating unit that provides reactive power serivce and has an ISA or WMPA with PJM would be eligible for compensation under Schedule 2. | FERC Determined with a requirement that resources file an annual report with FERC containing the financial and technical information that is used in the annual revenue requirement calculations, including the most recent power factor test results. Compensation should be adjusted automatically to reflect the power factor, if the demonstrated power factor is more than 0.01 higher than the power factor used to establish the current reactive power compensation (down only). Reactive power capability compensation should remain in place as long as a resource is providing reactive power capability. Once a resource is no longer providing reactive power capability, compensation should cease. | Compensation should be adjusted automatically to reflect the tested MVAR amounts (up or down). Reactive power capability compensation should remain in place as long as a resource is providing reactive power capability. Once a resource is no longer providing reactive power capability, compensation should cease.
1C2 | What is meant by a Transmission Facitliy? (MP1, Tariff Facility, BES) | High
2 | Reactive Capability Verification/Testing | Low - High | Varies (Manual 14D - Attachment E) | Nameplate | Testing by PJM | Annual testing plus assessment of actual performance during ops | Assessment of actual performance during ops | Testing with adjustments calculated for grid conditions at the time of testing | Every 5-years testing/demonstration | Power factor testing should be done at a defined real power output target value (for example, Summer Economic Maximum) while determining the reactive power capability target for the test and should occur at no less than the MOD-25 intervals. Testing must recognize that there may be seasonal or system conditions that pose limitations and which should be considered in analyzing test results.
3 | Delivery Point for Compensation and Related Purposes (e.g. Capability Testing) | Low - High | Varies (FERC Determined Delivery Point) | Exciter Terminals | POI | Match capability testing and ISA obligation | Nearest upstream PJM Transmission Facility bus | Exciter/Inverter Terminals | Nearest upstream PJM Transmission Facility bus (MVAR based on Telemetry)
4 | Treatment of Resources interconnected at Distribution Level (i.e., not PJM monitored facilities) that makes wholesale sales of electric energy in interstate commerce the PJM energy market | Medium | Varies | A: Identical to Transmission Resources; B: Not Eligible; C: Proportional Allocation to account for high impedance between DER terminals and PJM transmission facilities (i.e. the distribution system); D: Not Eligible for PJM
5 | Treatment of Capacitors (and other standalone VAR equipment) located at Generator Sites | Medium | Varies | A: Included in plant MVAR capability; B: Excluded in Plant MVAR capability; C: Included in plant MVAR capability if they meet technical conditions e.g. fast enough autonomous response to be useful post-contingency
6 | Cost development rules for non-synchronous resources if applicable | Medium | Varies | A: Not Applicable; B: A resource-specific, cost of service using the AEP methodology.; C: A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates periodically, at least every three years.
7 | Flat Rate Methodology | Medium - High | None | A: Nepool Approach; B: NY Approach; C: Avoided cost of SVC or similar; D: NEISO. Remove reactive revenue from Capacity Market pro forma modeling (i.e., remove from VRR CT Net CONE and Net ACR/MOPR Net CONE).; E: A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates periodically, at least every three years.
7A | Determinate used for flat rate |  |  | A: MVAR Capability beyond ISA obligation/requirement; B: All MVAR capability gets flat rate
8 | Performance incentive/penalty | Medium | None | A: Pass/fail/exceed with penalty/bonus structure; B: Overall performance score with tiered penalties for underperformance; C: Pass/fail with penalty; D: Overall performance score with tiered penalties for underperformance and bonus for overperformance; E: Monthly pass/fail look back analysis of generator voltage control performance.
8a | AVR | Low |  | A: In order to pass during an AVR outage must have a ticket and some demo that they can meet output.
9 | Eligibility for Reactive Services Uplift (Make Whole and Lost Opportunity Cost) | Low | Steam, CCGT, CTs, and Energy Storage Resources | A: All resources otherwise eligible for reactive capability compensation
10 | Voltage schedule development process | Medium |  | A: Set upon unit registration for reactive compenstion if not already identified
11 | Implementation |  |  | A: Capability payments only applies to new ISAs going forward

## 2a. Design Component Details
Reactive Power Compensation Task Force
Reactive Rate Process
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
Reactive Power Compensation Task Force
Reactive Rate Process
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
11E | Physically connect to PJM Transmission Facilities. Must have automatic voltage regulation operating at all times except for planned outaged. Requirement to be dispatched by PJM for reactive power as needed.
13F | Every 5-years testing/demonstration When internal conditions preclude testing (or demonstration within last 2 years) of full MVAR capability, only actual delivered MVAR will be eligible for flat rate payment. PJM reserves the right to require a retest if prior test capability is not reflected in actual operations. Limit 2 test per year
20E | Monthly pass/fail look back analysis of generator voltage control performance. If voltage at regulated bus exceeds voltage schedule high/low limits for a 5 mimute period, evaluate actual MVAR provided compared to expected MVAR. If actual MVAR is less than 90% of expected (lagging) or greater than 90% (leading), reactive flat rate revenues are withheld for following month and capability is reduced to match delivered. Generator may retest to increase capability. If voltage is consistently within voltage schedule, generator has assumed to pass test. Generators will only be evaluated when online. No excuse for unit online but AVR not in service. If they fail what would be next/how do they get their compenstion back if they fail?

## 3. Package Matrix
Reactive Power Compensation Task Force
Reactive Rate Process
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components1 | Priority | Status Quo | A | B | C | D | E
* | Compensation Mechanism | High | Unit specific related/structured to the AEP methodology, FERC settlement proceedings, and filed rate. Payment via PJM Tariff Schedule 2- FERC Filed Rate | Flat Rate | Streamlined AEP method. Two options: (A) unit-specific approach using AEP-based form; or (b) AEP-derived stated rate based on generation type | A resource-specific, i.e., generator, cost of service filed at FERC using the AEP methodology | A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates periodically, at least every three years.
1 | Basis for Compensation | High | FERC Approved Capability | MVAR Capability ISA | Cost-of-Service rate recovery. | n/a | n/a
2 | Treatment of leading vs. lagging capabillity. Lagging means injecting | High |  | Only lagging compensated | n/a | n/a | n/a
3 | Eligibility for Compensation | High | FERC Determined | Located inside PJM footprint | Any generating unit that provides reactive power serivce and has an ISA or WMPA with PJM would be eligible for compensation under Schedule 2. | FERC Determined with a requirement that resources file an annual report with FERC containing the financial and technical information that is used in the annual revenue requirement calculations, including the most recent power factor test results. Compensation should be adjusted automatically to reflect the power factor, if the demonstrated power factor is more than 0.01 higher than the power factor used to establish the current reactive power compensation (down only). Reactive power capability compensation should remain in place as long as a resource is providing reactive power capability. Once a resource is no longer providing reactive power capability, compensation should cease. | Compensation should be adjusted automatically to reflect the tested MVAR amounts (up or down). Reactive power capability compensation should remain in place as long as a resource is providing reactive power capability. Once a resource is no longer providing reactive power capability, compensation should cease.
4 | Reactive Capability Verification/Testing | Low | Varies (Manual 14D - Attachment E) | Not required but PJM needs to verify the generator can satisfy the ISA requirements | Manufacturer's technical specifications should be deemed adequate to support use of nameplate capability. | Power factor testing should be done at a defined real power output target value (for example, Summer Economic Maximum) while determining the reactive power capability target for the test and should occur at no less than the MOD-25 intervals. Testing must recognize that there may be seasonal or system conditions that pose limitations and which should be considered in analyzing test results. | n/a
5 | Delivery Point for Compensation and Related Purposes (e.g. Capability Testing) | High | Varies (FERC Determined Delivery Point) | Interconnection point with PJM transmission system | n/a | n/a | n/a
6 | Treatment of Resources interconnected at Distribution Level (i.e., not PJM monitored facilities) that makes wholesale sales of electric energy in interstate commerce the PJM energy market | Medium | Varies | Not eligible as these resources are not tranmission level facilities | Eligible for compensation under Schedule 2 | n/a | n/a
7 | Treatment of Capacitors (and other standalone VAR equipment) located at Generator Sites | High | Varies | Reactive capability not eligible for Schedule 2 payments. | Eligible for recovery under either compensation mechanism discussed above. | n/a | n/a
9 | Cost development rules for non-synchronous resources if applicable | Medium | Varies | Not required | Under Option A, the AEP-based form would be fuel neutral. Under Option B, a stated rate would be created for each generation type. | A resource-specific, cost of service using the AEP methodology. | A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates periodically, at least every three years. |  | Low
10 | Flat Rate Methodology | High | None | NEISO approach | AEP-derived stated rate based on generation type | A flat rate per MVAr that is differentiated by resource type, power factor and location determined using the AEP methodology with a requirement to update flat rates periodically, at least every three years. | n/a |  | Low - Medium
| Performance incentive/penalty | Medium |  | Yes | n/a | n/a | n/a
| Eligibility for Reactive Services Uplift (Make Whole and Lost Opportunity Cost) | Low | Steam, CCGT, CTs, and Energy Storage Resources | Yes | Synchronous and non-synchronous resource eligible for uplift. Additionally, mechanism should be created to compensate inverter-based resources for providing reactive power when resource is not providing real power. | n/a | n/a
| Voltage schedule development process | Medium |  | Yes | n/a | n/a | n/a
| Implementation |  |  | Rate applicable to all units. A transition rate would be established for those units ith existing FERC approved rates. | New reactive power compensation mechanism should be applied prosperctively following acceptance of PJM's FPA section 205 following by FERC. New reactive power compensation mechanism should not impact generating units that have rates on file with FERC, generating units that have a FPA section 205 filing pending at FERC at the time of filing, or projects that have a facilities study agreement signed by the interconnection customer | n/a | n/a
Medium
Medium - High
High

## 3a. Package Details
Reactive Power Compensation Task Force
Reactive Rate Process
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
Reactive Power Compensation Task Force
Reactive Rate Process
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
Reactive Power Compensation Task Force
Reactive Rate Process
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3