## 2017-2018 Parameters
2017-2018 RPM Base Residual Auction Planning Parameters | [5 empty] | 2014-06-02 | 777383-v4B
Added Post-Clearing BRA Credit Rates
| RTO | Updated Capacity Import Limits to account for Exceptions and updated NEDTS.
Installed Reserve Margin (IRM) | 15.7% | Updated DPL-South CETL to reflect 35 MW ICTR determination
Pool-Wide Average EFORd | 5.65%
Forecast Pool Requirement (FPR) | 1.0916
Demand Resource (DR) Factor | 0.953
Preliminary Forecast Peak Load | 164478.8
Short-Term Resource Procurement Target | 2.5% |  | 98813.21 | 41779.04 | 31287.22 | 15174.3 | 7300
Pre-Clearing BRA Credit Rate, $/MW | 38477.21 |  | 40062.77 | 34273.5 | 40062.77 | 40062.77 | 40062.77
LOCATIONAL DELIVERABILITY AREA (LDA)
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL
CETO | NA | 4420 | 6140 | 5880 | 6080 | 2370 | 1440 | 3740 | 4970 | 3350 | 2290 | 4350 | 1310
CETL | NA | 7393 | 9315 | 8053 | 6700 | 2795 | 1904 | 5359 | 8470 | 4940 | 7020 | 6217 | 4336
Reliability Requirement | 179545.0581 | 71534 | 39371 | 16935 | 12759 | 6465 | 3215 | 8715 | 16009 | 6250 | 28991 | 8701 | 10813
Total Peak Load of FRR Entities | 13318.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378.5 | 0 | 0
Preliminary FRR Obligation | 14538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.2 | 0 | 0
Reliability Requirement adjusted for FRR | 165007.1 | 71534 | 39371 | 16935 | 12759 | 6465 | 3215 | 8715 | 16009 | 6250 | 28991 | 8701 | 10813
Short-Term Resource Procurement Target | 4125.2 | 1655.1756 | 902.4038 | 381.5438 | 285.728 | 138.5781 | 66.1114 | 183.6355 | 357.0372 | 122.5219 | 629.5431 | 197.9083 | 205.1401
Net CONE, $/MW-Day (UCAP Price) | 351.39 | 313 | 365.87 | 313 | 365.87 | 365.87 | 365.87 | 313 | 373.75 | 373.75 | 373.75 | 313 | 354.46
Variable Resource Requirement Curve:
Point (a) UCAP Price, $/MW-Day | 527.085 | 469.5 | 548.805 | 469.5 | 548.805 | 548.805 | 548.805 | 469.5 | 560.625 | 560.625 | 560.625 | 469.5 | 531.69
Point (b) UCAP Price, $/MW-Day | 351.39 | 313 | 365.87 | 313 | 365.87 | 365.87 | 365.87 | 313 | 373.75 | 373.75 | 373.75 | 313 | 354.46
Point (c) UCAP Price, $/MW-Day | 70.28 | 62.6 | 73.17 | 62.6 | 73.17 | 73.17 | 73.17 | 62.6 | 74.75 | 74.75 | 74.75 | 62.6 | 70.89
Point (a) UCAP Level, MW | 156603.4 | 68024 | 37447.7 | 16114.3 | 12142.4 | 6158.8 | 3065.5 | 8305.4 | 15236.9 | 5965.4 | 27609.7 | 8277.5 | 10327.5
Point (b) UCAP Level, MW | 162308.1 | 70497.1 | 38808.9 | 16699.8 | 12583.5 | 6382.3 | 3176.7 | 8606.7 | 15790.3 | 6181.5 | 28612 | 8578.3 | 10701.3
Point (c) UCAP Level, MW | 168012.7 | 72970.2 | 40170 | 17285.3 | 13024.7 | 6605.8 | 3287.8 | 8908 | 16343.8 | 6397.6 | 29614.3 | 8879.1 | 11075.1
Participant-Funded ICTRs Awarded | NA | 159 | NA | 444 | NA | NA | 72 | 191 | NA | NA | NA | NA | NA
Post-Clearing BRA Credit Rate (LMT), $/MW | 7739.46 | 7739.46 | 7739.46 | 7739.46 | 14674.46 | 14674.46 | 7739.46 | 7739.46 | 7739.46 | 7739.46 | 7739.46 | 7739.46 | 7300
Post-Clearing BRA Credit Rate (ES), $/MW | 8760 | 8760 | 8760 | 8760 | 15695 | 15695 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 7300
Post-Clearing BRA Credit Rate (ANL), $/MW | 8760 | 8760 | 8760 | 8760 | 15695 | 15695 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
FRR Load Requirement (% Obligation):
Minimum Internal Resource Requirement | NA | 96.88% | 83.27% | 58.2% | 53.01% | 66.21% | 49.58% | 45.69% | 52.79% | 26.73% | 85.84% | 31.38% | 78.93%
LDA CETO/CETL Data; Zonal Peak Loads, Base Zonal FRR Scaling Factors, and Zonal Short-Term Resource Procurement Targets.
LDA/Zone | CETO | CETL | CETL to CETO Ratio % | 2013 Zonal W/N Coincident Peak Loads | Preliminary Zonal Peak Load Forecast | Base Zonal FRR Scaling Factor | Short-Term Resource Procurement Target | FRR Portion of the Preliminary Peak Load Forecast | Preliminary Zonal Peak Load Forecast less FRR load**
RTO | NA | NA | NA | 155456.6 | 164478.8 | NA | 4125.2 | 13318.1 | 151160.7
AE | 1130 | > 1300.0 | > 115% | 2590 | 2750 | 1.0618 | 75.0479 | 0 | 2750
AEP | 1260 | > 1449 | > 115% | 22670 | 23323 | 1.0288 | 308.5262 | 12017.6 | 11305.4
APS | 3740 | > 4301 | > 115% | 8270 | 8841 | 1.069 | 241.2723 | 0 | 8841
ATSI | 4970 | 8470 | 170.4% | 12680 | 13083 | 1.0318 | 357.0372 | 0 | 13083
ATSI-CLEVELAND | 3350 | 4940 | 147.5% | NA | 4489.6 | NA | 122.5219 | 0 | 4489.6
BGE | 4350 | 6217 | 142.9% | 6920 | 7252 | 1.048 | 197.9083 | 0 | 7252
COMED | 2290 | 7020 | 306.6% | 21830 | 23447 | 1.0741 | 629.5431 | 378.5 | 23068.5
DAYTON | 970 | > 1116 | > 115% | 3260 | 3503 | 1.0745 | 95.5974 | 0 | 3503
DEOK | 3760 | > 4324 | > 115% | 5270 | 5533 | 1.0499 | 126.3562 | 902.9 | 4630.1
DLCO | 1520 | > 1748 | > 115% | 2820 | 2976 | 1.0553 | 81.2155 | 0 | 2976
DOM | -540 | * | * | 18980 | 20978 | 1.1053 | 572.493 | 0 | 20978
DPL | 980 | > 1127 | > 115% | 3970 | 4184 | 1.0539 | 114.182 | 0 | 4184
DPL SOUTH | 1440 | 1869 | 129.8% | NA | 2422.536 | NA | 66.1114 | 0 | 2422.536
EKPC | 250 | > 288 | > 115% | 2051.6 | 2143.8 | 1.0449 | 57.9834 | 19.1 | 2124.7
JCPL | 3370 | > 3876 | > 115% | 6020 | 6369 | 1.058 | 173.811 | 0 | 6369
METED | 1290 | > 1484.0 | > 115% | 2840 | 3061 | 1.0778 | 83.5352 | 0 | 3061
PECO | 3260 | > 3749 | > 115% | 8360 | 8881 | 1.0623 | 242.3639 | 0 | 8881
PENLC | 600 | > 690 | > 115% | 2770 | 3025 | 1.0921 | 82.5527 | 0 | 3025
PEPCO | 3740 | 5359 | 143.3% | 6520 | 6729 | 1.0321 | 183.6355 | 0 | 6729
PL (incl. UGI) | 1310 | 4336 | 331% | 7115 | 7517 | 1.0565 | 205.1401 | 0 | 7517
PS | 6080 | 6700 | 110.2% | 10120 | 10470 | 1.0346 | 285.728 | 0 | 10470
PS NORTH | 2370 | 2795 | 117.9% | NA | 5077.95 | NA | 138.5781 | 0 | 5077.95
RECO | NA | NA | NA | 400 | 413 | 1.0325 | 11.2708 | 0 | 413
EMAAC | 6140 | 9315 | 151.7% | NA | 33067 | NA | 902.4038 | 0 | ** Used to allocate Short-Term Resource Procurement Target to Zones.
SWMAAC | 5880 | 8053 | 137% | NA | 13981 | NA | 381.5438 | 0
Western MAAC | -5010 | * | * | NA | 13603 | NA | 371.2281 | 0
MAAC | 4420 | 7393 | 167.3% | NA | 60651 | NA | 1655.1756 | 0
Western PJM | 8210 | > 9442 | > 115% | NA | 82849.8 | NA | 1897.5314 | 13318.1
* LDA has adequate internal resources to meet the reliability criterion.
Limiting conditions at the CETL for modeled LDAs:
LDA | Violation/Limiting Facility
MAAC | Thermal / Brister - Ox 500 kV circuit
EMAAC | Voltage / Voltage collapse for the loss of the Keeney - Rock Springs 500 kV circuit.
SWMAAC | Voltage / Voltage collapse for the loss of Burches Hill - Possum Point 500 kV circuit.
PS | Thermal / Roseland - Wilpipe 230 kV circuit.
PSNORTH | Thermal / Roseland - Wilpipe 230 kV circuit.
DPLSOUTH | Thermal/Easton - Trappe Tap 69 kV circuit.
PEPCO | Voltage / Voltage collapse for the loss of Burches Hill - Possum Point 500 kV circuit.
ATSI | Thermal / South Canton - Harmon 345 kV circuit.
ATSI-CLEVELAND | Thermal / South Canton - Harmon 345 kV circuit.
COMED | Thermal / University Park - East Frankfort 345 kV circuit.
BGE | Thermal / Pumphrey 230/115 kV transformer.
PL | Thermal / Wescosville 500/138 kV transformer.

## Net CONE
RPM CONE and E&AS Values for 2017/2018 Base Residual Auction
ICAP to UCAP Conversion Factor:
UCAP Price = ICAP Price/(1 - Pool-Wide Average EFORd)
Pool-Wide Average EFORd for 2017/2018 = | 5.65%
CONE Area 1: AE, DPL, JCPL, PECO, PS, RECO
CONE Area 2: BGE, PEPCO
CONE Area 3: AEP, APS, ATSI, ComEd, Dayton, DEOK, Duquesne (DLCo), EKPC
CONE Area 4: MetEd, Penelec, PPL
CONE Area 5: Dominion
MAAC CONE used is the lowest of the three CONE Areas 1, 2, and 4.
| CONE Area 1 | CONE Area 2 | CONE Area 3 | CONE Area 4 | CONE Area 5 | MAAC: Used Area 2 CONE | RTO
Benchmark CONE (2016/2017 BRA Value): Levelized Revenue Requirement, $/MW-Year | 152460 | 142223.4 | 139485 | 146470.5 | 124919.5 | 142223.4 | 139392
12 Months Handy Whitman Index (July 1, 2013) | 2.9% | 2.9% | 3% | 2.9% | 2.9% | 2.9% | 2.9%
Region basis for the Handy Whitman Index | North Atlantic | North Atlantic | North Central | North Atlantic | South Atlantic | North Atlantic | North Atlantic
2017/2018 BRA CONE, escalated by Handy Whitman Index, $/MW-Year | 156881.34 | 146347.8786 | 143669.55 | 150718.1445 | 128542.1655 | 146347.8786 | 143434.368
Gross CONE, $/MW-Day, UCAP Price | 455.55 | 424.96 | 417.19 | 437.65 | 373.26 | 424.96 | 416.5
Historic (2011-2013) Net Energy Revenue Offset, $/MW-Year | 28686 | 36360 | 12761 | 26452 | 26492 | 36360 | 20224
Zonal LMP used for Net Energy Offset Calculation | AE Zonal LMP | BGE Zonal LMP | ComEd Zonal LMP | MetEd Zonal LMP | Dominion Zonal LMP | BGE Zonal LMP | PJM Average LMP
Ancillary Services Offset, $/MW-Year per Tariff | 2199 | 2199 | 2199 | 2199 | 2199 | 2199 | 2199
Net CONE, $/MW-Day, ICAP Price | 345.1955 | 295.312 | 352.6289 | 334.4305 | 273.5648 | 295.312 | 331.538
Net CONE, $/MW-Day, UCAP Price | 365.87 | 313 | 373.75 | 354.46 | 289.95 | 313 | 351.39
VRR Curve Point (a) UCAP Price, $/MW-Day * | 548.805 | 469.5 | 560.625 | 531.69 | 434.925 | 469.5 | 527.085
* VRR Curve Point (a) UCAP Price is the higher of 1.5 Net CONE or Gross CONE.

## Key Transmission Upgrades
New Key Transmission Upgrades included for 2017/2018 model
Upgrade ID | Description | Transmission Owner
b0497 | Install a second Conastone - Graceton 230 kV circuit and replace Conastone 230 kV breaker 2323/2302 | BGE
b1016 | Rebuild Graceton - Bagley 230 kV as double circuit line using 1590 ACSR. Terminate new line at Graceton with a new circuit breaker. | BGE
b1251 | Rebuild the existing Bagley - Raphael Rd. 230 kV line to double circuit 230 kV line | BGE
b1251.1 | Reconfigure Raphael Rd. to terminate new circuit | BGE
b1813.6 | Build approximately 14 miles new 230 kV Jenkins-Acahela 230 kV Line | PPL
b2015 | Build a new 230 kV circuit from Larrabee to Oceanview | JCPL
b2136 | Reconductor the Morgantown - V3-017 230 kV '23086' circuit and replace terminal equipments at Morgantown | PEPCO
b2137 | Reconductor the Morgantown - Talbert 230 kV '23085' circuit and replace terminal equipments at Morgantown | PEPCO
b2141 | Construct a new Byron to Wayne 345 kV circuit | ComEd
b2228 | +150/-100 MVAR SVC at Cedar 230 kV | AEC
b2360 | Build a new 39 mile 230 kV transmission line from Dooms - Lexington on existing right-of-way | Dominion
b2361 | Construct 230 kV OH line along existing Line #2035 corridor, approx. 2.4 miles from Idylwood - Dulles Toll Road (DTR) and 2.1 miles on new right-of-way along DTR to new Scott's Run Substation | Dominion
b2362 | Install a 250 MVAR SVC at Squab Hollow 230 kV | APS
b2364 | Install a new 230/138kV transformer at Squab Hollow 230kV substation. Loop the Forest - Elko 230 kV line into Squab Hollow. Loop the Brookville - Elko 138 kV line into Squab Hollow. | APS
b2449 | Rebuild the 7-mile 345 kV line between Meadow Lake and Reynolds 345 kV stations | AEP
Key Transmission Upgrades included for 2016/2017 model but not included for 2017/2018 model
Upgrade ID | Description | Transmission Owner
None

## DR Rel Targets
2017/2018 Demand Resource Constraints
Forecast Pool Requirement | 1.0916
Demand Resource Factor | 0.953
Quantities are in Unforced Capacity Megawatts | PJM Region | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL
Reliability Requirement adjusted for FRR | 165007.1 | 71534 | 39371 | 16935 | 12759 | 6465 | 3215 | 8715 | 16009 | 6250 | 28991 | 8701 | 10813
CETL | NA | 7393 | 9315 | 8053 | 6700 | 2795 | 1904 | 5359 | 8470 | 4940 | 7020 | 6217 | 4336
Preliminary Peak Load Forecast | 164478.8 | 60651 | 33067 | 13981 | 10470 | 5077.95 | 2422.536 | 6729 | 13083 | 4489.6 | 23447 | 7252 | 7517
FRR Peak Load | 13318.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378.5 | 0 | 0
Peak Load Forecast adjusted for FRR | 151160.7 | 60651 | 33067 | 13981 | 10470 | 5077.95 | 2422.536 | 6729 | 13083 | 4489.6 | 23068.5 | 7252 | 7517
Short-Term Resource Procurement Target | 4125.2 | 1655.1756 | 902.4038 | 381.5438 | 285.728 | 138.5781 | 66.1114 | 183.6355 | 357.0372 | 122.5219 | 629.5431 | 197.9083 | 205.1401
Limited Demand Resource Reliability Target
Percent of Preliminary Forecast Peak Load | 4.1% | 6.1% | 6.3% | 7.1% | 7% | 7% | 5.9% | 6.5% | 5.2% | 5.2% | 5.4% | 7.2% | 5.4%
Unforced Capacity, MW | 6447.3193 | 3848.7901 | 2167.164 | 1032.6497 | 762.4321 | 369.7795 | 148.6889 | 455.0093 | 707.7292 | 242.8664 | 1295.8942 | 543.1837 | 422.2744
Limited Resource Constraint | 2322.1193 | 2193.6145 | 1264.7602 | 651.1059 | 476.7041 | 231.2015 | 82.5775 | 271.3738 | 350.692 | 120.3445 | 666.3511 | 345.2754 | 217.1342
Sub-Annual Resource Reliability Target
Percent of Preliminary Forecast Peak Load | 9.3% | 11.5% | 16.7% | 15.2% | 19.1% | 15.3% | 13.6% | 14.9% | 17.3% | 24.7% | 26.5% | 15.4% | 5.5%
Unforced Capacity, MW | 14624.4072 | 7255.9158 | 5744.7045 | 2210.743 | 2080.3503 | 808.2324 | 342.7406 | 1043.0214 | 2354.5606 | 1153.6154 | 6359.4808 | 1161.8096 | 430.0943
Sub-Annual Resource Constraint | 10499.2072 | 5600.7402 | 4842.3007 | 1829.1992 | 1794.6223 | 669.6544 | 276.6292 | 859.3859 | 1997.5234 | 1031.0934 | 5729.9377 | 963.9013 | 224.9541
DR Constraints for FRR Load (ICAP as % of peak load)
Limited Resource Constraint | 4.1% | 6.1% | 6.3% | 7.1% | 7% | 7% | 5.9% | 6.5% | 5.2% | 5.2% | 5.4% | 7.2% | 5.4%
Sub-Annual Resource Constraint | 9.3% | 11.5% | 16.7% | 15.2% | 19.1% | 15.3% | 13.6% | 14.9% | 17.3% | 24.7% | 26.5% | 15.4% | 5.5%

## Cap Import Limits
2017/2018 Capacity Import Limits in Megawatts
External Source Zone
| Simultaneous | North | West 1 | West 2 | South 1 | South 2
Capacity Import Limit (CIL) for use in BRA * | 1524.3 ** | 27 | 0 | 397 | 188 | 0
Confirmed NEDTS as of 5/6/2014 | 9801 | 105 | 3063 | 4623 | 1190 | 820
Approved CIL Exception Requests | 4776.7 | 0 | 1916.2 | 2683 | 0 | 177.5
* The calculated CIL to be entered into the RPM Auction reflect adjustments for the quantity of CIL Exceptions that PJM has granted and the Capacity Benefit Margin.
** The simultaneous limit is greater than the sum of the individual External Source Zone limits and will therefore not constrain imports.