## Planning Parameters
2024-2025 RPM Base Residual Auction Planning Parameters |  |  | 2024-05-08
| RTO | Notes:
Installed Reserve Margin (IRM) | 14.7% | 2021 IRM Study, endorsed at the October 20, 2021 MRC meeting...https://pjm.com/planning/resource-adequacy-planning/reserve-requirement-dev-process
Pool-Wide Average EFORd | 5.02% | 2021 IRM Study, endorsed at the October 20, 2021 MRC meeting.
Forecast Pool Requirement (FPR) | 1.0894 | 2021 IRM Study, endorsed at the October 20, 2021 MRC meeting.
Preliminary Forecast Peak Load | 150640.3154 | 2022 Load Report with adjustments for load served outside PJM.
Locational Deliverability Area
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL | DAYTON | DEOK
CETO | NA | -4760 | 2740 | 6060 | 5630 | 2560 | 1420 | 4220 | 5080 | 3560 | -4570 | 4660 | -30 | 2470 | 3270
CETL | NA | 5965 | 8594 | 7947 | 8287 | 4253 | 2009 | 7033 | 10465 | 4941 | 4640.4 | 5397 | 4337 | 3918 | 4999
Reliability Requirement | 164107.6 | 63518 | 35415 | 14299 | 11166 | 5715 | 3514 | 7151 | 14434 | 5374 | 23859 | 7514 | 10214 | 3922 | 6881
Total Peak Load of FRR Entities | 29421.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 787.9243
Preliminary FRR Obligation | 32051.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 858.4
Reliability Requirement adjusted for FRR | 132055.7 | 63518 | 35415 | 14299 | 11166 | 5715 | 3514 | 7151 | 14434 | 5374 | 23859 | 7514 | 10214 | 3922 | 6589.144
Gross CONE, $/MW-Day (UCAP Price) | 348.94 | 351.93 | 355.14 | 357.45 | 355.14 | 355.14 | 355.14 | 357.45 | 341.33 | 341.33 | 341.33 | 357.45 | 341.83 | 341.33 | 341.33
Net CONE, $/MW-Day (UCAP Price) | 293.19 | 294.06 | 312.39 | 261.07 | 321.21 | 321.21 | 284.11 | 288.07 | 279.35 | 279.35 | 302.76 | 234.07 | 297.25 | 262.17 | 268.26
EE Addback (UCAP) | 7667.2 | 3392.3 | 1906.7 | 766.2 | 676.5 | 329.5 | 99.8 | 387.6 | 579.6 | 54.9 | 1063.3 | 378.6 | 377.6 | 127 | 183.9
Variable Resource Requirement Curve:
Point (a) UCAP Price, $/MW-Day | 439.79 | 441.09 | 468.59 | 391.61 | 481.82 | 481.82 | 426.17 | 432.11 | 419.03 | 419.03 | 454.14 | 357.45 | 445.88 | 393.26 | 402.39
Point (b) UCAP Price, $/MW-Day | 219.89 | 220.55 | 234.29 | 195.8 | 240.91 | 240.91 | 213.08 | 216.05 | 209.51 | 209.51 | 227.07 | 175.55 | 222.94 | 196.63 | 201.2
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Point (a) UCAP Level, MW | 138341.3 | 66245.8 | 36951.2 | 14915.6 | 11725.7 | 5984.7 | 3577 | 7463.8 | 14862.6 | 5372.7 | 24672.7 | 7814 | 10484.7 | 4008 | 6704.1
Point (b) UCAP Level, MW | 141910.4 | 67962.5 | 37908.3 | 15302.1 | 12027.5 | 6139.2 | 3672 | 7657.1 | 15252.7 | 5517.9 | 25317.5 | 8017.1 | 10760.8 | 4114 | 6882.2
Point (c) UCAP Level, MW | 148703.1 | 71229.7 | 39730 | 16037.6 | 12601.8 | 6433.1 | 3852.8 | 8024.9 | 15995.2 | 5794.4 | 26544.8 | 8403.6 | 11286.2 | 4315.7 | 7221.1
Nominated PRD Value, MW | 305 | 305 | 35 | 270 | 0 | 0 | 13 | 110 | 0 | 0 | 0 | 160 | 0 | 0 | 0
VRR Curve adjusted for PRD:
Point (a1) UCAP Price, $/MW-Day | 439.79 | 441.09 | 468.59 | 391.61 |  |  | 426.17 | 432.11 |  |  |  | 357.45
Point (b1) UCAP Price, $/MW-Day | 219.89 | 220.55 | 234.29 | 195.8 |  |  | 213.08 | 216.05 |  |  |  | 175.55
Point (prd1) UCAP Price, $/MW-Day | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01 |  |  |  | 0.01
Point (prd2) UCAP Price, $/MW-Day | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01 |  |  |  | 0.01
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  | 0
Point (a1) UCAP Level, MW | 138009 | 65913.5 | 36913.1 | 14621.5 |  |  | 3562.8 | 7344 |  |  |  | 7639.7
Point (b1) UCAP Level, MW | 141578.1 | 67630.2 | 37870.2 | 15008 |  |  | 3657.8 | 7537.3 |  |  |  | 7842.8
Point (prd1) UCAP Level, MW | 148370.5 | 70897.3 | 39691.8 | 15743.5 |  |  | 3838.6 | 7905.1 |  |  |  | 8229.3
Point (prd2) UCAP Level, MW | 148702.8 | 71229.6 | 39729.9 | 16037.6 |  |  | 3852.8 | 8024.9 |  |  |  | 8403.6
Point (c) UCAP Level, MW | 148703.1 | 71229.7 | 39730 | 16037.6 |  |  | 3852.8 | 8024.9 |  |  |  | 8403.6
Pre-Auction Credit Rate, $/MW | 53507.18 | 53665.95 | 57011.18 | 47645.28 | 58620.83 | 58620.83 | 51850.08 | 52572.78 | 50981.38 | 50981.38 | 55253.7 | 42717.78 | 54248.13 | 47846.03 | 48957.45
Post-Auction Credit Rate, $/MW | 53507.18 | 53665.95 | 57011.18 | 47645.28 | 58620.83 | 58620.83 | 31110.41 | 52572.78 | 50981.38 | 50981.38 | 55253.7 | 42717.78 | 54248.13 | 47846.03 | 48957.45
Participant-Funded ICTRs Awarded | NA | 1557 | 40 | NA | 1070 | 639 | 72 | NA | NA | NA | 1376 | 65.7 | NA | NA | 155
FRR Load Requirement (% Obligation):
Minimum Internal Resource Requirement | NA | 97.7% | 83.3% | 48.8% | 28.5% | NA | 58.5% | NA | 30.3% | NA | 89% | 31.3% | NA | NA | 34%
LDA CETO/CETL Data; Zonal Peak Loads, Base Zonal FRR Scaling Factors, and FRR load.
LDA/Zone | CETO (Capacity Emergency Transfer Objective) | CETL (Capacity Emergency Transfer Limit) | CETL to CETO Ratio % | 2021 Zonal W/N Coincident Peak Loads | Preliminary Zonal Peak Load Forecast | Base Zonal FRR Scaling Factor | FRR Portion of the Preliminary Peak Load Forecast | Preliminary Zonal Peak Load Forecast less FRR load | LDA/Zone
RTO | NA | NA | NA | 148881.4 | 150640.3154 | NA | 29421.6189 | 121218.6965 | RTO
AE | 1740 | >2,001.0 | >115% | 2430 | 2399 | 0.98724 | 0 | 2399 | AE
AEP | -2730 | * | * | 21304.3 | 21659 | 1.0166 | 10611.0729 | 11047.9271 | AEP
APS | 1500 | >1,725.0 | >115% | 8440 | 8535 | 1.0113 | 0 | 8535 | APS
ATSI | 5080 | 10465 | 206% | 11860 | 12014 | 1.013 | 0 | 12014 | ATSI
ATSI-CLEVELAND | 3560 | 4941 | 138.8% | NA | 4156.844 | NA | 0 | NA | ATSI-CLEVELAND
BGE | 4660 | 5397 | 115.8% | 6180 | 6211 | 1.005 | 0 | 6211 | BGE
COMED | -4570 | 4640.4 | * | 20290 | 19827 | 0.97718 | 0 | 19827 | COMED
DAYTON | 2470 | 3918 | 158.6% | 3150 | 3149 | 0.99968 | 0 | 3149 | DAYTON
DEOK | 3270 | 4999 | 152.9% | 4990 | 5087 | 1.0194 | 787.9243 | 4299.0757 | DEOK
DLCO | 1560 | >1,794.0 | >115% | 2660 | 2678 | 1.0068 | 0 | 2678 | DLCO
DOM | 2810 | >3,231.5 | >115% | 19447.9 | 21128 | 1.0864 | 18000.0665 | 3127.9335 | DOM
DPL | 690 | >793.5 | >115% | 3760 | 3787 | 1.0072 | 0 | 3787 | DPL
DPL SOUTH | 1420 | 2009 | 179.4% | NA | 2363.088 | NA | 0 | 2363.088 | DPL SOUTH
EKPC | 1240 | >1,426.0 | >115% | 2309.2 | 2411.3154 | 1.0442 | 22.5552 | 2388.7602 | EKPC
JCPL | 3070 | >3,530.5 | >115% | 5700 | 5585 | 0.97982 | 0 | 5585 | JCPL
METED | 980 | >1,127.0 | >115% | 2890 | 2859 | 0.98927 | 0 | 2859 | METED
OVEC | NA | NA | NA | 70 | 70 | 1 | 0 | 70 | OVEC
PECO | 2530 | >2,909.5 | >115% | 8140 | 8131 | 0.99889 | 0 | 8131 | PECO
PENLC | -570 | * | * | 2780 | 2708 | 0.9741 | 0 | 2708 | PENLC
PEPCO | 4220 | 7033 | 166.7% | 5750 | 5734 | 0.99722 | 0 | 5734 | PEPCO
PL (incl. UGI) | -30 | 4337 | * | 7080 | 7030 | 0.99294 | 0 | 7030 | PL (incl. UGI)
PS | 5630 | 8287 | 165.3% | 9270 | 9264 | 0.99935 | 0 | 9264 | PS
PS NORTH | 2560 | 4253 | 163.7% | NA | 4817.28 | NA | 0 | 4817.28 | PS NORTH
RECO | NA | NA | NA | 380 | 374 | 0.98421 | 0 | 374 | RECO
EMAAC | 2740 | 8594 | 319.7% | NA | 29540 | NA | 0 |  | EMAAC
SWMAAC | 6060 | 7947 | 131.1% | NA | 11945 | NA | 0 |  | SWMAAC
Western MAAC | -10060 | * | * | NA | 12597 | NA | 0 |  | Western MAAC
MAAC | -4760 | * | * | NA | 54082 | NA | 0 |  | MAAC
Western PJM | -7250 | * | * | NA | 75430.3154 | NA | 11421.5524 |  | Western PJM
* LDA has adequate internal resources to meet the reliability criterion.
Limiting conditions at the CETL for modeled LDAs:
LDA | Violation |  | Limiting Facility
MAAC | Thermal |  | Doubs - Brighton 500 kV for the loss of Burches Hill - Possum Point 500 kV
EMAAC | Voltage |  | Voltage drop at Black Oak 500 kV for the loss of the 500/138 kV transformer, SVC and Capacitor at Black Oak
SWMAAC | Voltage |  | Voltage collapse for the loss of Conastone - Brighton 500 kV line
PS | Thermal |  | Brunswick - Meadow Road 230 kV ckt Z2331 for the loss of Metuchen -Pierson Ave - Meadow Rd- Deans 230 kV ckt s2219 Aldene - Stanley Terrance 230kV for the loss of WEST ORANGE - ORANGE HEIGHTS 230 kV Roseland - Williams 230 kV for the loss of Roseland - Cedar Grove 230 kV
PSNORTH | Thermal |  | Aldene - Stanley Terrance 230kV for the loss of WEST ORANGE - ORANGE HEIGHTS 230 kV Aldene - Stanley Terrance 230kV for the loss of ALDENE TO SPRINGFIELD ROAD 230 kV ROSELAND - Williams PIPE 230 kV for the loss of Roseland - Cedar Grove 230 kV
DPLSOUTH | Thermal |  | Cedar Creek - Silver Run 230 kV for the loss of Cartanza - Silver Run 230 kV Keeney - Rock Springs 500 kV for the loss of Peach Bottom - Limerick 500 kV
PEPCO | Thermal |  | Brighton - Waugh Chapel 500 kV for the loss of Burches Hill - Possum Point 500 kV Chalk Point 500/230 kV transformer for the loss 223983 CHALK230 230 1 for Chalk Point 230 kV bus tie safe Horbor - Graceton 230 kV for the loss of Peach Bottom - Conastone 500 kV North West - Conastone 230 kV ckt 2310 for the loss of the North West - Conastone 230 kV ckt 2322
ATSI | Thermal |  | TIDD - Collier 345 kV for the loss of Wylie Ridge - Toronto 345 kV line
ATSI-CLEVELAND | Voltage |  | Voltage drop at Crestwood Q-1 and Crestwood Q-3 for the loss of ATSI_P1-2_CEI-138-006A_SRT-A
COMED | Thermal |  | Mitchell-Wilson 138 kV line for the loss of the Cabot-Keystone 500 kV line Bosserman-Michigan City 138 kV line for the loss of the Bosserman-Trail Creek 138 kV line New Carlisle-Bosserman 138 kV circuit No. 2 for the loss of the New Carlisle-Bosserman 138 kV circuit No.1 South Bend 138 kV bus tie for the loss of the Olive 345/138 kV No. 2 transformer Gosney Hill-Stull Run 138 kV for the loss of the Kammer 765/500 kV No. 5 transformer Krendale-Shanor Manor 138 kV for the loss of the Cabot-Cranberry 500 kV line
BGE | Voltage |  | Voltage collapse for the loss of the Conastone - Brighton 500 kV line
PL | Thermal |  | Eldred - Sunbury 230 kV for the loss of Montour - Columbia 230 kV Wescosville 500/230 kV transformer pre-contingency
DAYTON | Thermal |  | Shelby - Sidney 138 kV for the loss of the Miami - West Milton -Miami Fort 345 kV
DEOK | Thermal |  | PeachBottom-Conastone 500 kv Line pre contingency Beckjord - Pierce 138kV line for the loss of Pierce - Foster 345 kv line

## Net CONE
RPM CONE and E&AS Values for 2024/2025 Base Residual Auction
ICAP to UCAP Conversion Factor:
UCAP Price = ICAP Price / (1 - Pool-Wide Average EFORd)
Pool-Wide Average EFORd for 2023/2024 BRA | [6 empty] | 5.02%
CONE Area 1: AE, DPL, JCPL, PECO, PS, RECO
CONE Area 2: BGE, PEPCO
CONE Area 3: AEP, APS, ATSI, ComEd, Dayton, DEOK, Dominion, Duquesne (DLCo), EKPC, OVEC
CONE Area 4: MetEd, Penelec, PPL
Zone/LDA | 2023/2024 BRA CONE: Levelized Revenue Requirement, $/MW-Year * | Escalation | 2024/2025 BRA CONE: Levelized Revenue Requirement, $/MW-Year | Gross CONE, $/MW-Day, UCAP Price | Historic Net Energy Revenue Offset, $/MW-Year | Ancillary Services Offset, $/MW-Year per Tariff | Net E&AS Revenue Offset, $/MW-Year | Net CONE, $/MW-Day, ICAP Price | Net CONE, $/MW-Day, UCAP Price | LDA Modeled with VRR Curve
CONE Area 1 | 115311.3127 | 1.0677 | 123117.5818 | 355.14
AE |  |  |  | 355.14 | 9847.31 | 2199 | 12046.31 | 304.3049 | 320.39
DPL |  |  |  | 355.14 | 22422.45 | 2199 | 24621.45 | 269.8524 | 284.11 | DPL SOUTH
JCPL |  |  |  | 355.14 | 9798.49 | 2199 | 11997.49 | 304.4386 | 320.53
PE |  |  |  | 355.14 | 9905.77 | 2199 | 12104.77 | 304.1447 | 320.22
PSEG |  |  |  | 355.14 | 9563.04 | 2199 | 11762.04 | 305.0837 | 321.21 | PS, PSEG NORTH
RECO |  |  |  | 355.14 | 14195.31 | 2199 | 16394.31 | 292.3925 | 307.85
EMAAC |  |  |  | 355.14 |  |  |  | 296.71 | 312.39 | EMAAC
CONE Area 2 | 116593.1938 | 1.0628 | 123919.5337 | 357.45
BGE |  |  |  | 357.45 | 40572.89 | 2199 | 42771.89 | 222.3223 | 234.07 | BGE
PEPCO |  |  |  | 357.45 | 21852.59 | 2199 | 24051.59 | 273.6108 | 288.07 | PEPCO
SWMAAC |  |  |  | 357.45 |  |  |  | 247.96 | 261.07 | SWMAAC
CONE Area 4 | 111813.5832 | 1.0598 | 118504.999 | 341.83
METED |  |  |  | 341.83 | 20830.9 | 2199 | 23029.9 | 261.5756 | 275.4
PENELEC |  |  |  | 341.83 | 24250.94 | 2199 | 26449.94 | 252.2056 | 265.54
PPL |  |  |  | 341.83 | 13256.42 | 2199 | 15455.42 | 282.3276 | 297.25 | PPL
MAAC |  |  |  | 351.93 |  |  |  | 279.3 | 294.06 | MAAC
CONE Area 3 | 111730.7823 | 1.0591 | 118329.5519 | 341.33
AEP |  |  |  | 341.33 | 24383.12 | 2199 | 26582.12 | 251.3628 | 264.65
APS |  |  |  | 341.33 | 29845.91 | 2199 | 32044.91 | 236.3963 | 248.89
ATSI |  |  |  | 341.33 | 19285.96 | 2199 | 21484.96 | 265.3276 | 279.35 | ATSI, ATSI CLEVELAND
COMED |  |  |  | 341.33 | 11171.73 | 2199 | 13370.73 | 287.5584 | 302.76 | COMED
DAYTON |  |  |  | 341.33 | 25243.89 | 2199 | 27442.89 | 249.0046 | 262.17 | DAYTON
DEOK |  |  |  | 341.33 | 23130.93 | 2199 | 25329.93 | 254.7935 | 268.26 | DEOK
DLCO |  |  |  | 341.33 | 22846.92 | 2199 | 25045.92 | 255.5716 | 269.08
DOM |  |  |  | 341.33 | 22540.06 | 2199 | 24739.06 | 256.4123 | 269.96
EKPC |  |  |  | 341.33 | 17126.23 | 2199 | 19325.23 | 271.2447 | 285.58
OVEC |  |  |  | 341.33 | 21325.25 | 2199 | 23524.25 | 259.7406 | 273.47
RTO | 113862.218 |  | 120967.9166 | 348.94 | 17127.74 | 2199 | 19326.74 | 278.469 | 293.19 | RTO
* The 2023/2024 BRA CONE values are based on PJM’s Quadrennial Review filing (Docket No. ER19-105) which was FERC approved on April 15, 2019.

## Key Transmission Upgrades
New Key Transmission Upgrades included for 2024/2025 model
Upgrade ID | Description | Transmission Owner
b3021 | Rebuild 500kV Line #581 Ladysmith to Chancellor - 15.2 miles long | Dominion
b3332 | Rerate the 23076 Steel-Milford 230 kV line | DPL
b3698 | Reconductor the 14.2 miles of the existing Juniata-Cumberland 230 kV line with 1272 ACSS/TW HS285 "Pheasant" conductor. | PPL
b3321 | Rebuild Cranes Corner-Stafford 230 kV line | Dominion
b3318 | Reconductor the Shanor Manor - Butler 138 kV line with an upgraded circuit breaker at Butler | APS
Key Transmission Upgrades included for 2023/2024 model but not included for 2024/2025 model
Upgrade ID | Description | Transmission Owner
None