## BKR Rating Template
SUBSTATION EQUIPMENT RATING WORKSHEET
VI_C Circuit Breaker Ratings ANNEX II - SAMPLE 230 KV, 4000A, POST-1964, CLASS A INSULATION
Circuit Breaker
1) Populate the nameplate information table as fully as possible
NAMEPLATE
STATION
EQUIPMENT |  |  | Circuit Breaker |  |  | Note: Correct system voltage must be entered for corresponding MVA values in the table below.
TYPE
YEAR MANUF.
MANUFACTURER |  |  | 1976
POSITION |  |  | ----
DESIGNATION |  |  | ----
RATED VOLTAGE (KV) |  |  | 230
RATED CURRENT (A) |  |  | 4000
2) Identify a material class and complete the input table
| Breakers manuf. Prior to 1964 | [5 empty] | Breakers manuf. 1964 and later
| 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6
qmax e4 | 85 | 90 | 110 | 135 | 85 | 95 | 105 | 120 | 120 | 165
qmax | 70 | 75 | 95 | 120 | 70 | 80 | 90 | 105 | 105 | 150
qr | 30 | 35 | 55 | 80 | 30 | 40 | 50 | 65 | 65 | 110
INPUT
qmax e4 | 120 |  |  | Rating |  | Summer 35o C |  | Winter 10o C
qmax | 105 |  |  |  |  | MVA | Amps | MVA | Amps
qr | 65 |  |  | Normal |  | 1660.4616 | 4168.1215 | 1967.4772 | 4938.7977
I Rated | 4000 |  |  | Emergency (4Hr) |  | 1849.5828 | 4642.857 | 2134.4275 | 5357.8796
Rated KV | 230
CALCULATED RATINGS
AMBIENT TEMP. |  | RATING ( P.U. ) |  |  |  | RATING ( MVA ) |  |  | RATINGS (AMPS)
qa | qa |  |  | Load |  |  |  | Load |  |  | Laod
Deg. C | Deg. F | NORMAL | 4 HOUR | Dump |  | NORMAL | 4 HOUR | Dump | NORMAL | 4 HOUR | Dump
0 | 32 | 1.3053 | 1.4058 | 1.8918 |  | 2079.9712 | 2240.1395 | 3014.5713 | 5221.1822 | 5623.2397 | 7567.2329
5 | 41 | 1.2704 | 1.373 | 1.8257 |  | 2024.3494 | 2187.7944 | 2909.1687 | 5081.5595 | 5491.842 | 7302.6493
10 | 50 | 1.2347 | 1.3395 | 1.7575 |  | 1967.4772 | 2134.4275 | 2800.618 | 4938.7977 | 5357.8796 | 7030.1632
15 | 59 | 1.1982 | 1.3053 | 1.6872 |  | 1909.2581 | 2079.9712 | 2688.5913 | 4792.6552 | 5221.1822 | 6748.9518
20 | 68 | 1.1607 | 1.2704 | 1.6145 |  | 1849.5828 | 2024.3494 | 2572.6986 | 4642.857 | 5081.5595 | 6458.0357
25 | 77 | 1.1223 | 1.2347 | 1.5391 |  | 1788.3256 | 1967.4772 | 2452.4692 | 4489.088 | 4938.7977 | 6156.2336
30 | 86 | 1.0827 | 1.1982 | 1.4605 |  | 1725.3415 | 1909.2581 | 2327.3266 | 4330.9843 | 4792.6552 | 5842.0985
35 | 95 | 1.042 | 1.1607 | 1.3785 |  | 1660.4616 | 1849.5828 | 2196.5514 | 4168.1215 | 4642.857 | 5513.8242
40 | 104 | 1 | 1.1223 | 1.2923 |  | 1593.4867 | 1788.3256 | 2059.2252 | 4000 | 4489.088 | 5169.1053