## Notes
2020/21 RTEP Long-Term Window
Revision History:
| Revised Posting Date: | 2021-05-03
| Original Posting Date: | 2021-01-11
| Version of this file: | 6
| V6: | Removed ME-1 Kammer to Natrium 138 kV from the list of eligible congestion drivers for the 2020/21 RTEP Market Efficiency Window: 1. After the mid-cycle update, congestion on Kammer to Natrium 138 kV decreases close to 50% in the 2025 simulated year, and more than 60% in the 2028 simulated year. 2. FSA Sensitivity shows annual congestion less than $1 million in 2025 simulated year.
| V5: | Removed ME-4 Yukon to AA2-161 Tap 138 kV, and ME-8 Harwood to Susquehanna 230 kV from the list of eligible congestion drivers for the 2020/21 RTEP Market Efficiency Window: 1. Suspension of AA2-161 unit eliminates the congestion driver on Yukon to AA2-161 Tap 138 kV. 2. Congestion on Harwood to Susquehanna 230 kV decreases more than 65% in each of the 2025 and 2028 years after modeling the market impact of DLR (Dynamic Link Rating) project (Expected in-service date 06/01/2021). Congestion decreases between simulated years 2025 and 2028. FSA Sensitivity shows annual congestion less than $1 million in 2028 simulated year. Harwood to Susquehanna 230 kV driver may also be impacted by recently announced Talen Energy retirements. (Retirement notice not submitted to PJM).
| V4: | Removed ME-2 Muskingum River to Beverly 345 kV, ME-9 Duff to Francisco 345 kV, and ME-10 Gibson to Francisco 345 kV from the list of eligible congestion drivers for the 2020/21 RTEP Market Efficiency Window: 1. A sag study completed by the TO eliminated the Muskingum River to Beverly 345 kV congestion driver. 2. A planned MISO upgrade, MTEP ID 20345, significantly decreased congestion on the Duff to Francisco 345 kV, and Gibson to Francisco 345 kV M2M drivers.
| V3: | Added note: A sag study being performed by the TO may decrease or eliminate the Muskingum River to Beverly 345 kV congestion driver.
| V2: | Posted conductor ratings provided by TOs for eligible congestion drivers that are limited by station equipment
| V1: | Window Open

## Eligible Congestion Drivers
2020/21 RTEP Market Efficiency Window Eligible Energy Market Congestion Drivers (Reposted 05-03-2021) |  |  |  | ME Base Case (Annual Congestion $million) |  | ME Base Case (Hours Binding)
FG# | Constraint | FROM AREA | TO AREA | 2025 Simulated Year | 2028 Simulated Year | 2025 Simulated Year | 2028 Simulated Year | Line is Conductor Limited? | Conductor Ratings* | Comment | Potential Upgrades
ME-3 | Junction to French's Mill 138 kV | APS | APS | 15.2389 | 15.7152 | 342 | 317 | No | SN/SE=221/268 MVA WN/WE=250/317 MVA | Internal Flowgate
ME-5 | Charlottesville to Proffit Rd Del Pt 230 kV | DOM | DOM | 7.3397 | 10.2521 | 164 | 169 | Yes |  | Internal Flowgate
ME-6 | Plymouth Meeting to Whitpain 230 kV | PECO | PECO | 4.0331 | 2.7635 | 78 | 89 | No | SN/SE=463/578 MVA WN/WE=521/639 MVA | Internal Flowgate
ME-7 | Cumberland to Juniata 230 kV | PLGRP | PLGRP | 9.3048 | 10.1027 | 209 | 217 | Yes |  | Internal Flowgate | Cumberland – Juniata congestion driver may be impacted by DLR (Dynamic Link Rating) project (Expected in-service date 06/01/2021).
*Conductor ratings provided by TOs for congestion drivers that are limited by station equipment.