3/2/2021 Update

AEP Update:

AEP corrected WE rating for the Leesville – Altavista 138kV line, see “Altavista-Leesville (Winter)_Rev1.idv”. With the updated ratings, the FG# GD-W9, GD-W10, GD-W11, GD-W12, and GD-W13 are not violations anymore, therefore are removed from the posted results.

AEP corrected ratings for Natrium bus 2, see “Natrium-138-Z2-Ratings-Correction_Winter.idv” and “Natrium-138-Z2-Ratings-Correction_Summer.idv”, which doesn’t change any posted flowgates.

AEP corrected breaker contingency definition for ratings for CONTINGENCY 'AEP_P4_#13198_05HAYSI 69.0_F', see “AEP_P4_#13198_05HAYSI 69.0_F correction.con”, which doesn’t change any posted flowgates.

AEP corrected Dunkirk cap status, see “Switch ON Dunkirk Cap.idv”. With the update, the FG# AEP-VM810 and AEP-VM811 are not violations anymore, therefore are removed from the posted results.

AEP delete the invalid contingency “AEP_P5_#11299_05OHIO_05OHIO”, see “Delete Ohio Central P5 INVALID.con”. With the contingency deletion, the FG# AEP-VD421, AEP-VD422, and AEP-VD423 are not violations anymore, therefore are removed from the posted results.

AEP-VD416, AEP-VD417, AEP-VD418, AEP-VD419, AEP-VD420, AEP-VD1140, AEP-VD1141, AEP-VD1146, and AEP-VD1147 are driven by S1996. Additional scope of S1996 will be investigated to solve the issues through M-3 process. Comments are updated accordingly.

AEP corrected INCO reactive load model, see “INCO_Load_Correction.idv”. With the load correction, the FG# AEP-VM725, AEP-VM726, AEP-VM789, AEP-VM790, AEP-VM791, and AEP-VM792 are not violations anymore, therefore are removed from the posted results.

AEP corrected winter load model for Pikeville area, see “PikevilleAreaLoadUpdateWIN.idv”, which doesn’t change any posted flowgates.

AEP provided corrected contingency definitions, see” AEP_P1-2_#15286_modified.con”, “AEP_P1-3_#12526_05NFINDL 138_1_modified.con”, “AEP_P4_#7765_05NFINDL _138_B_modified.con”, and “AEP_P4_#10110_05EBERSO 138_A_modified.con”. With the updated contingency definitions, the FG# AEP-VM511 through AEP-VM515, AEP-VM530 through AEP-VM538 and AEP-VD484 through AEP-VD497 are not violations anymore, therefore are removed from the posted results.

AEP provided a case correction, posted on 11/25/2020, correcting Vhi for the cap banks at Killbuck, see “Change Kilbuck caps Vhi.idv”. Additionally, AEP provided a case adjustment for  winter case to  turn off Killbuck cap, see “Turn off Killbuck cap bank.idv”. With the changes, FG# AEP-VM458 and AEP-VM459 are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case correction to open the normally open 46kV line between Middle Creek and Falcon, see “FalconNO.idv”. With the correction, FG# AEP-VM540 through AEP-VM544, and AEP-VD498 through AEP-VD501 are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case adjustment, posted on 10/22/2020, on the shunt device at Whetstone Station, see “WBasset & Fieldale CapSettings.IDV”, FG# AEP-VM473, and AEP-VM478, are no longer valid violations, therefore they are removed from the posted results.

AEP provided corrected contingency definitions for contingencies AEP_P1-3_#12196_05E CAMBRD 69.0_1  and AEP_P1-3_#11754_05WCAMBR 138_2 , see ”Cambridge XF Con Corrections.con”. With the correction, FG# AEP-VD739 through AEP-VD746, AEP-VD764, AEP-VD769, AEP-VD773, AEP-VD775, AEP-VD874 through AEP-VD881, and AEP-VD886 through AEP-VD889 are no longer valid violations, therefore they are removed from the posted results.

AEP corrected Radford load correction, see “RemoveRadfordLoad.idv”. With the load correction, the FG# AEP-VD1025, AEP-VD1027, AEP-VD1054, AEP-VD1055, and AEP-VD1056 are not violations anymore, therefore are removed from the posted results.

AEP provided corrected contingency definitions for contingency AEP_P1-3_#11298_05REUSENS1 138_4, see “ReusensT4.con”. With the contingency correction, the FG# AEP-VD789, AEP-VD803, AEP-VD815, AEP-VD821, AEP-VD912, AEP-VD959, AEP-VD960, AEP-VD961, and AEP-VD1003 are not violations anymore, therefore are removed from the posted results.

AEP provided a correction for Stanville cap bank voltage band, see “Stanville 69kV Cap Bank.idv”. It would resolve the voltage issues under the N-1-1 scenario for FG#, AEP-VD786, therefore it is removed from the posted results.

AEP provided a switching solution, switching on cap banks at East Wooster after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FG#, AEP-VD1100, therefore it is removed from the posted results.

The FG# AEP-VD1109 is solved by B3110 new scope, presented 7/17/2020 Western SRRTEP. The comments for FG# AEP-VD1109 is updated accordingly.

AEP updated the initial value of Glade shunt, see “Glade Binit.idv”, which doesn’t change any posted flowgates.

AEP corrected load model at Patrick, see “Patrick.idv”, which doesn’t change any posted flowgates.

ComEd Update:

The cancellation of S1533 on 7/17/2020, see “s1533 Rochelle.idv”” and “Remove s1533 Rochelle.con”, removes the thermal violation in light load. The comments for FG# GD-LL33 is updated accordingly.

11/25/2020 Update

AEP Update:

AEP provided a switching solution, closing the normally open switch at East Tiffin after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FG#, AEP-T16, AEP-T17, AEP-T18, AEP-T19 and AEP-T20, therefore they are removed from the posted results.

AEP corrected the ratings for Waterford – Muskingum 345kV line, Jefferson – Clifty 345kV line, East Lima 345/138kV transformer #2, and Olive - Carlisle 138kV line, see Jefferson-Clifty_345_ WIN_WithMultiplier(rev).idv”, “Jefferson-Clifty_345_SUM_WithMultiplier(rev).idv”, “EastLima _345-138_WIN_WithMultiplier_LDDerate(rev).idv”, “EastLima_345- 138_SUM_WithMultiplier (rev).idv”, “Waterford-Muskingum_345_WIN_WithMultiplier_LDDerate.idv”, “Waterford-Muskingum_345_SUM_WithMultiplier_LDDerate.idv”, “New Carlisle-Olive_138_WIN_With Multiplier.idv”, “New Carlisle-Olive_138_SUM_WithMultiplier.idv”, and “Con updates for multipliers.con”. With the updated ratings, the FG# GD-S301, GD-W183, GD-W6, N1-W-T17, N2-ST16, N2-ST17, N2-ST18; N2-ST19, N2-ST20, N2-ST21, N2-ST22, GD-S2, GD-S3, GD-S4, GD-S5, GD-S8, and GD-S14 are not violations anymore, therefore are removed from the posted results.

AEP provided a switching solution, switching on Mark Center Cap bank after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FG#, AEP-VD971, AEP-VD972, AEP-VD973, AEP-VD974 and AEP-VD983, therefore they are removed from the posted results.

AEP provided a switching solution, switching on cap banks at Ripley, Ravenswood and Hemlock after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FG#, AEP-VD27, AEP-VD28, AEP-VD29,AEP-VD30, AEP-VD31, AEP-VD32, AEP-VD33, AEP-VD34, AEP-VD35, AEP-VD36, AEP-VD37, AEP-VD38, AEP-VD39, AEP-VD40, AEP-VD424, AEP-VD425, AEP-VD426, AEP-VD427, AEP-VD428, AEP-VD429, and AEP-VD430, therefore they are removed from the posted results.

AEP provided a switching solution, switching on cap banks at East Wooster after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FG#, AEP-VD1057, AEP-VD1058, AEP-VD1059, AEP-VD1060, AEP-VD1061, AEP-VD1062, AEP-VD1063, AEP-VD1064, AEP-VD1065, AEP-VD1066, AEP-VD1067, AEP-VD1068, AEP-VD1069, AEP-VD1070, AEP-VD1071, AEP-VD1072, AEP-VD1073, AEP-VD1074, AEP-VD1075, AEP-VD1076, AEP-VD1077, AEP-VD1078, AEP-VD1079, AEP-VD1080, AEP-VD1081, AEP-VD1082, AEP-VD1083, and AEP-VD1101, therefore they are removed from the posted results.

AEP provided a switching solution, switching on cap banks at Gemini after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FG# AEP-VD910 and AEP-VD911, therefore they are removed from the posted results.

AEP provided a case adjustment, switching off 34.5 kV capacitor banks at N. Findlay Bus#1, N. Findlay Bus #2 and N. Baltimore 34.5 kV buses, see “Findlay Area Cap Banks.idv”. FG# AEP-VM516 through AEP-VM529 and AEP-VM539, are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case adjustment, changing the tap setting on Hyatt 138/34.5kV transformer bank 2, see “Hyatt_Volt_Mag_138kV XF2.idv”. FG# AEP-VM469 is no longer valid violations, therefore they are removed from the posted results.

AEP provided a case correction, purging duplicated load D3 and reduce Mvar on the remaining distribution loads, see “Groves Road 13.8kV_Voltage Drop.idv”. FG# AEP-VD593, AEP-VD594, AEP-VD595, AEP-VD596, AEP-VD597, AEP-VD598, AEP-VD599, and AEP-VD600 are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case correction, switching off the cap bank at LaRue, see “La Rue Cap Off.idv”. FG# AEP-VD706, AEP-VD709, AEP-VD710, AEP-VD711, AEP-VD712, AEP-VD713, AEP-VD714, AEP-VD715, and AEP-VD716 are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case correction, correcting Vhi for the cap banks at Killbuck, see “Change Kilbuck caps Vhi.idv”. Additionally, AEP provided a case adjustment for summer case to turn on the cap bank at Killbuck, see “Killbuck Cap on.idv”, and a case adjustment for winter case to  turn off Killbuck cap, see “Turn off Killbuck cap bank.idv”. FG# AEP-VM460, AEP-VM461, AEP-VM462, AEP-VM463, AEP-VM464, AEP-VM465, AEP-VM466, AEP-VM467, AEP-VM468, AEP-VD360, AEP-VD361, AEP-VD362, AEP-VD363, AEP-VD372, AEP-VD375, AEP-VD402, AEP-VM454, AEP-VM455, AEP-VM456 andAEP-VM457 are no longer valid violations, therefore they are removed from the posted results.

10/22/2020 Update

AEP Update:

AEP provided a switching solution, closing the normally open tie between Dominion and AEP (bus #313704 to bus #242658) after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FG#, AEP-VM854 and AEP-VD1164, therefore they are removed from the posted results.

AEP provided a contingency update, removing invalid contingency “AEP_P2-1_242640 05FLOYD 138 243969 05FLOYD EQ 999 1”, see “Floyd Transformer.con”.  FG# AEP-VM474, AEP-VM492, AEP-VD436, AEP-VD438, AEP-VD474 and AEP-VD475 are no longer valid violations, therefore they are removed from the posted results.

AEP provided a contingency update, removing invalid contingency “AEP_P1-2_#5700_9206”, see “Deleted Holston #5700-9206.CON”.  FG# AEP-VM81, AEP-VM84, AEP-VD1004, AEP-VD1005, AEP-VD1006, AEP-VD1007, AEP-VD1008, AEP-VD1009, AEP-VD1010, AEP-VD1011, AEP-VD1014, AEP-VD1015, AEP-VD1016, AEP-VD1017, AEP-VD1018, AEP-VD1019, AEP-VD1020, AEP-VD1021, AEP-VD621, AEP-VD622, AEP-VD623, AEP-VD625, AEP-VD626, and AEP-VD627 are no longer valid violations, therefore they are removed from the posted results.

The buses 05SOUTHSID, 05SCHOOLFI, 05BRIDGE S, 05RIVERSD, 05PINEYFOR, 05WESTOVER, 05WEST FOR, 05NEW DESI, 05WHITMELL, and 05WHITE OA are not AEP buses. They are owned by City of Danville. Therefore, the associate flowgates, FG# AEP-VD804, AEP-VD805, AEP-VD806, AEP-VD807, AEP-VD808, AEP-VD809, AEP-VD813, AEP-VD822, AEP-VD823, AEP-VD824, AEP-VD825, AEP-VD826, AEP-VD827, AEP-VD828, AEP-VD831, AEP-VD832, AEP-VD834, AEP-VD836, AEP-VD837, AEP-VD839, AEP-VD841, AEP-VD842, AEP-VD845, AEP-VD846, AEP-VD847, AEP-VD848, AEP-VD849, AEP-VD850, AEP-VD851, AEP-VD852, AEP-VD854, AEP-VD855, AEP-VD856, AEP-VD857, AEP-VD858, AEP-VD861, AEP-VD862, AEP-VD913, AEP-VD914, AEP-VD915, AEP-VD917, AEP-VD918, AEP-VD919, AEP-VD922, AEP-VD924, AEP-VD925, AEP-VD926, AEP-VD927, AEP-VD928, AEP-VD929, AEP-VD930, AEP-VD931, AEP-VD932, AEP-VD933, AEP-VD934, AEP-VD935, AEP-VD936, AEP-VD937, AEP-VD938, AEP-VD939, AEP-VD940, AEP-VD941, AEP-VD942, AEP-VD943, AEP-VD944, AEP-VD945, AEP-VD946, AEP-VD947, AEP-VD949, AEP-VD950, AEP-VD951, AEP-VD952, AEP-VD953, AEP-VD954, AEP-VD955, AEP-VD957, and AEP-VD958, are no longer valid AEP 715 violations, therefore they are removed from the posted results.

AEP provided a contingency correction, see ”Hales Br.CON”. FGs# AEP-VM233, AEP-VM234, AEP-VD228, AEP-VD229, AEP-VD232, AEP-VD233, AEP-VD235, AEP-VD236, AEP-VD237, AEP-VD238, AEP-VD242, AEP-VD243, AEP-VD244, AEP-VD245, AEP-VD247, AEP-VD249, AEP-VD250, and AEP-VD251 are no longer valid violations, therefore they are removed from the posted results.

AEP provided a switching solution, locking Cap bank at S. Bluefield (Bus 242784) after the first contingency. It would resolve the voltage issue under the N-1-1 scenario for FG# AEP-VM852, therefore they are removed from the posted results.

AEP provided a switching solution, locking Cap bank off at Sullivan (Bus 242819) after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FGs# AEP-VM57, AEP-VM58, AEP-VM59, AEP-VM60, AEP-VM61, AEP-VM62, AEP-VM63, AEP-VM64, AEP-VM65, AEP-VM66, AEP-VM67, AEP-VM68, AEP-VM69, AEP-VM70, AEP-VM71, AEP-VM72, AEP-VM73, AEP-VM74, AEP-VM75, AEP-VM76, AEP-VM77, AEP-VM78, AEP-VM79, AEP-VM80, AEP-VM82, AEP-VM83, AEP-VM85, AEP-VM86, AEP-VM87, and AEP-VM882, therefore they are removed from the posted results.

AEP provided a case correction updating incorrect transformer ratings on the transformer tertiary and a case adjustment modifying the transformer tap ratio, see “Floyd Transformer.idv”. FG# AEP-VM484, AEP-VM485, AEP-VM486, AEP-VM487, AEP-VM488, AEP-VM489, AEP-VM490, AEP-VM491, AEP-VM493, AEP-VM494, AEP-VM495, AEP-VM496, AEP-VM497, AEP-VM498, AEP-VM499, AEP-VM500, and AEP-VM501, are no longer valid violations, therefore they are removed from the posted results.

AEP provided two case adjustments, updating the shunt device at Morgan Fork and updating the tap ratio at Beaver Creek on transformer #2, see “Morgan Fork Cap Bank (Beaver Creek Bus tie breaker solution).idv” and “Beaver Creek Ratio.idv”. FG# AEP-VD364, AEP-VD365, AEP-VD366, AEP-VD367, and AEP-VD480, are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case correction updating the line impedance for New Cast – Meadow C, New Cast –Stone Coal Gap and Stone Coal Gap – Mt. Union 34.5kV lines, see “StoneCoalGap.idv”, which doesn’t change any posted flowgates.

AEP provided a switching solution, locking the Mt Union 69kV cap bank after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FGs# AEP-VD1105, AEP-VD1106, and AEP-VD1107, therefore they are removed from the posted results.

AEP provided a case adjustment on the shunt device at Whetstone Station. The case adjustment at Garden Creek updates the transformer tap ratio, see “Whetstone Branch Cap Bank (Garden Creek Breaker L failure solution).idv” and “Garden Creek CBL Soln.idv”. FG# AEP-VD619, AEP-VD994, AEP-VD995, AEP-VD996, AEP-VD997, AEP-VD998, and AEP-VD999, are no longer valid violations, therefore they are removed from the posted results.

AEP provided an updated comments on FGs: AEP-T453, AEP-T458, AEP-T459, AEP-T452, AEP-T460, AEP-T447, AEP-T442, AEP-T443, AEP-T444, AEP-T446, and AEP-T445. “Associated with AEP-2020-IM020 and AEP-2019-IM044”

AEP provided a summer emergency rating correction for Leesville – Altavista 138kV line “AEP-Summer_leesville - Altavista 138kV SE rating correction.idv”, which doesn’t change any posted flowgates.

AEP provided a case adjustment on the shunt device at Whetstone Station and  the transformer tap ratio at Garden Creek transformer, see “WBasset & Fieldale CapSettings.IDV” and “Martinsville Ratio.idv”, FG# AEP-VM470, AEP-VM475, AEP-VM481, AEP-VM472, AEP-VM477, AEP-VM483, AEP-VM471, AEP-VM476, AEP-VM482, AEP-VM479, and AEP-VM480, are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case adjustment on the Sheridan Cap shunt to have it on in the base case, see “Sheridan Cap Bank.idv”. FG# AEP-VD702, and AEP-VD1090, are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case correction modeling the load served on the Reedy Creek 69kV bus and eliminating the 12 kV bus, see “Reedy Creek 12kV.idv”. FG# AEP-VD592, AEP-VD601, AEP-VD620, and AEP-VD624, are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case adjustment on the shunt device at Point Pleasant, see “Point Pleasant Cap.idv”, FG# AEP-VD584 through AEP-VD591, and AEP-VD660 through AEP-VD667, are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case adjustment on the transformer tap ratio at Pleasant transformer, see “Pleasant XF tap change.idv”, which doesn’t change any posted flowgate.

AEP provided a case adjustment on the shunt device at Radford, see “Lock Radford 34.5 kV Cap ON.idv”. FG# AEP-VD1035, AEP-VD1038, AEP-VD1039, AEP-VD1040, AEP-VD1044, AEP-VD688, AEP-VD689, AEP-VD690, AEP-VD692, AEP-VD698, AEP-VD1036, AEP-VD1041, AEP-VD1042, AEP-VD1043, AEP-VD1045, AEP-VD685, AEP-VD686, AEP-VD687, AEP-VD691, AEP-VD697, AEP-VD1024, AEP-VD1052, AEP-VD1026, AEP-VD1053, AEP-VD1032, AEP-VD1033, AEP-VD1034, AEP-VD1037, AEP-VD1108, AEP-VD693, AEP-VD694, AEP-VD695, AEP-VD696, AEP-VD699, and AEP-VD367, are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case adjustment on the shunt devices at Packsville and Dameron, see “Dameron_Cap_2.idv”. FG# AEP-VD1001, and AEP-VD1000, are no longer valid violations, therefore they are removed from the posted results.

AEP provided case adjustments on the shunt devices at Toms Fork, Kincaid, and Ronda and the transformer tap ratio at Pax Branch transformer, see “Toms Fork Caps.IDV” and “PaxBranchTap.idv”. FG# AEP-VD352, AEP-VD353, AEP-VD368, AEP-VD369, AEP-VD370, AEP-VD371, AEP-VD1094, AEP-VD1095, AEP-VD1096, and AEP-VD1097, are no longer valid violations, therefore they are removed from the posted results.

AEP provided a case adjustment at Sprigg to update the transformer #1 tap ratio, see “Sprigg Ratio.idv”, which doesn’t change any posted flowgate.

Dayton Update:

A case correction from PJM to correct voltage schedule for AC1-085, see “AC1-085 voltage schedule to align with AB1-169.idv”, which doesn’t change any posted flowgates.

9/18/2020 Update

AEP Update:

AEP provided a switching solution, closing the normally open tie between Dominion and AEP (bus #313704 to bus #242658) after the first contingency. It would resolve the voltage issues under the N-1-1 scenario for FG# AEP-VM846, AEP-VM847, AEP-VM848, AEP-VM849,  AEP-VM850, AEP-VM851, AEP-VM853, AEP-VD1162, AEP-VD1139, AEP-VD1144,  AEP-VD1163, AEP-VD1138, and AEP-VD1143, therefore they are removed from the posted results.

AEP provided a case correction on South Toronto switch, which is a normally open in the case that should be closed, see 2025RTEP-close-South-Toronto-connection.idv.  FG# AEP-T190, AEP-T191, AEP-T195, AEP-T196, AEP-T203, AEP-T204, AEP-T209, AEP-T210, AEP-T214, AEP-T215, AEP-T216, AEP-T217, AEP-VD628, AEP-VD629, AEP-VD1028, AEP-VD1029, AEP-VD1030, AEP-VD1031 are no longer valid violations, therefore they are removed from the posted results. Additionally, closing the South Toronto switch causes additional violations and the new flowgates will be posted in 2020 Window #3.

AEP provided a rating correction on ManbachSS to 10th Street 69kV branch, see “MansbachSS to 10th Street SUM MLSE.idv” and “MansbachSS to 10th Street WIN MLSE.idv”. FG# AEP-T251 and AEP-T252 are no longer valid violations, therefore they are removed from the posted results.

9/2/2020 Update

AEP Update:

AEP provided a rating correction on Lancaster Junction and a hard tap point in the 69 kV network named  05LANCAS JTZ in the case, see “Amos-Culloden_Correction_Summer.idv” and “Lancaster Junction To Lancaster JTZ Modeling Correction_Summer.idv”.  FG# AEP-T380 and AEP-T381 are no longer valid violations, therefore they are removed from the posted results.

The contingency “AEP_P5_#11282_05S BE_05S BE “ is invalid and has been removed. The FG# AEP-VD668 - AEP-VD680, AEP-VD683, and AEP-VD717 – AEP-VD721 are removed accordingly.

AEP provided rating corrections for the Amos – Culloden 765 kV line and the Amos 345/138 #7 transformer, see “Amos-Culloden_Correction_Summer.idv”, “Amos- Culloden_Correction_Winter.idv”, “AmosTF7_Summer_Correction.idv”, and “AmosTF7_Winter_Correction.idv”. FG# GD-W181, GD-W192 and N1-W-T14 are no longer valid violations, therefore they are removed from the posted results.

8/27/2020 Update

ATSI Update:

Identified additional 16 ATSI FERC 715 violations (ATSI-LLVM101-ATSI-LLWM116) and removed 26 ATSI FERC 715 violations (ATSI-LLVM1 – ATSI-LLVM11 and ATSI-LLVM23 – ATSI-LLVM37). New and removed FERC 715 violations are all 69 kV Light load voltage magnitude issues. PJM worked with ATSI to verify impacts of model updates that resulted in slight changes in voltages, resulting in several flowgates exceeding and others to decrease below their established FERC 715 high voltage limits. The flowgates are excluded from accepting proposals due to below 200kV exclusion.

8/25/2020 Update

JCPL Update:

Identified additional four overdutied 34.5 kV circuit breakers at Freneau substation (FG# JCPL-SC18, JCPL-SC19, JCPL-SC20 and JCPL-SC21).  FE/JCPL submitted the initial violation with incorrect modeling of the breaker protection group description.  PJM worked with First Energy and updated the breaker models to complete the required analysis and has now completed validating the violations. The flowgates are excluded from accepting proposals due to below 200kV exclusion.

8/18/2020 Update

AEP Update:

S1295 was inappropriately removed from the 2025 cases, see “J.Ferry-Pipers_Summer.idv” and “J.Ferry-Pipers_Winter.idv” and “JacksonsFerry-PipersGap138kV.con” for the model. With S1295  modeled in, FG# AEP-T140, AEP-T141, AEP-T142, AEP-T147, AEP-T74, AEP-T132, AEP-T299, AEP-T300, AEP-T301, AEP-T302 are no longer overloaded and therefore PJM is no longer accepting proposals. Additionally, FG# AEP-VD439, AEP-VD440, AEP-VD441, AEP-VD442, AEP-VD443, AEP-VD444, AEP-VD445, AEP-VD446, AEP-VD447, AEP-VD448, AEP-VD449, AEP-VD450, AEP-VD451, AEP-VD452, AEP-VD453, AEP-VD454, AEP-VD455, AEP-VD456, AEP-VD457, AEP-VD458, AEP-VD459, AEP-VD460, AEP-VD461, AEP-VD462, AEP-VD463, AEP-VD464, AEP-VD465, AEP-VD466, AEP-VD467, AEP-VD468, AEP-VD469, AEP-VD470, AEP-VD471, AEP-VD472, AEP-VD473, AEP-VD476, AEP-VD477, AEP-VD478, AEP-VD479, AEP-VD630, AEP-VD631, AEP-VD844, AEP-VD853, AEP-VD1102, AEP-VD1103, and AEP-VD1104 are not valid violations anymore, therefore removed from the posted results.

Following the initial build of the 2025 RTEP cases, S1295 was replaced with S2179, which will also continue to resolve the same violations as indicated above.

8/7/2020 Update

AEP Update:

Comments were updated for FG# GD-S298, GD-S446, GD-S315, N1-ST41, and N1-ST42 to include substation equipment exclusion.

Comments were corrected for FG# AEP-VD364, AEP-VD365. AEP-VD366 and AEP-VD367 and Below 200 kV exclusion was added.

AEP provided a correction for the impedance and ratings on 05N MID PT – 05VAN WER 69kVline and 05N MID PT – 05DELPHOS 69kV line, See “s_1617_correction_Summer.idv” and “s_1617_correction_Winter.idv” for the model correction. Due to the model correction, FG# AEP-T173, AEP-T174, AEP-T175, AEP-T176, AEP-T177, AEP-T178, AEP-T179, AEP-T180, AEP-T181, AEP-T186, AEP-T188, AEP-T192, AEP-T197, AEP-T198, AEP-T199, AEP-T200, AEP-T201, AEP-T202, AEP-T415, AEP-T434, and AEP-T437 are no longer overloaded and therefore PJM is no longer accepting proposals.

AEP provided a correction for the Vhi limit for 05Bridgeman 69kV switching shunt, See “AEP 05Bridgeman shunt band correction.idv” for the model correction. Due to the model correction, FG# AEP-VD658, AEP-VD659, AEP-VD1086 and AEP-VD1087 are not valid violations.

AMPT Update:

AMPT acquired 3.55 mile of Brewster – Harmon 69kV transmission line and substation facilities at the Brewster substation. This facility addition to AMPT facilities will requires AMPT to submit an AMPT FERC 715 MW-mile baseline violation. Please see “AMPT Brewster Load Update.idv” for explicit load modeling (load was netted)

7/30/2020 Update

AEP Update:

Comments were updated for FG# N2-SLD1.

AEP corrected the impedance and ratings of the 0523RD ST – 05BASF Z 35 kV line, 0526TH ST – 0524TH ST 35KV line and 0526TH ST – 05DARRAH 35KV line . See ‘East Huntington Ratings Corrections Summer.idv’ and “East Huntington Ratings Corrections Winter.idv” for the model correction.  Due to the model correction, FG# AEP-T253, AEP-T256, AEP-T421, AEP-T422, AEP- T456 and AEP-T457 are no longer overloaded and therefore PJM is no longer accepting proposals; and due to the conductor rating corrections, FG# AEP-T257, AEP-T258, AEP-T259, AEP-T266, AEP-T269, AEP-T270, AEP-T273, and AEP-T274 are determined to be violations associated with substation equipment. Additionally due to the removal of these previously identified flowgates (AEP-T257 through AEP-T274), the following flowgates, AEP-T277, AEP-T278, AEP-T279, and AEP-T280 are excluded from accepting proposals due to below 200kV exclusion.

Comments were updated to correct the errors in the spreadsheet for FG # AEP-T83, AEP-T85, AEP-T86 and AEP-T87.

Comments for FG# AEP-T171, AEP-T172, AEP-T354 and AEP-T355 were updated to correct errors and indicated these are solved by existing baseline project B3099, therefore, PJM is NOT accepting proposals.

Comments were for FG# AEP-T143, AEP-T144 AEP-T145, and AEP-T146 to correct errors. No changes to the status of accepting proposals.

Due to the removal of previously identified flowgate AEP-T139, the following flowgates, AEP-T31, AEP-T32, AEP-T33, AEP-T34, AEP-T35, AEP-T36, and AEP-T407 are excluded from accepting proposals due to below 200kV exclusion.

AEP provided a contingency correction “Abingdon_Correction.con”, which doesn’t change any posted flowgates

Dominion Update:

Comments were updated for FG# DOM-VM17, DOM-VD37 and DOM-VD38 to indicate that PJM has validate these issues.

7/24/2020 Update

RECO Update:

The following flowgates are removed due to modeling correction. See ‘RECO_South Mahwah transformer change.idv’ for the model correction.

FG#

N2-WVM20

N2-WVM21

N2-WVM22

N2-WVM23

N2-WVM24

N2-WVM25

N2-WVM26

N2-WVM27

AEP Update:

AEP FERC FORM 715 – FG# AEP-T139 is removed due to modeling correction. AEP corrected the impedance of the 05HOWARD – 05NGALIOSS 69 kV line. See ‘Howard - N_Galion Sw Impedance Correction.idv’ for the model correction.

APS Update:

APS FERC FORM 715 – in the ‘FERC Form 715 Voltage Drop’ tab, added comments on column P to indicate that PJM is not accepting proposals.

Dominion Update:

Dominion flowgates DOM-VM18 - DOM-VM26 are removed because system adjustments between events resolve the issues.

Dominion flowgates DOM-VD39 - DOM-VD47 are removed because system adjustments between events resolved the issues.

7/15/2020 Update

PPL Update:

PPL FERC Form 715 - FG# PPL-T1 and PPL-T2 are removed due to modeling correction/change.

PPL transferred load from South Akron to the nearby Lauschtown substation. See ‘SAKR_Load-Transfer.idv’ for the model correction.

PECO Update:

PECO FERC Form 715 – FG# PECO-T1 is removed due to modeling correction/change. See ‘PECO_Cromby summer load correction.idv’ for the model correction.

PECO updated/changed load model on the Cromby station. The substation forecast that was used to build the 2020 RTEP case, included a large customer (PE-2019-0002) at Cromby substation that is now being removed in the latest substation forecast. The PE-2019-0002 Need is canceled.

AEC Update:

FG# N2-ST23, N2-ST24, N2-ST35 and N2-ST36 are removed due to model correction. AEC corrected line impedance on the Monroe – Glasboro 69 kV circuit. See ‘Monroe-Glasboro 69 kV correction.idv’ for the model correction.

AEP Update:

AEP submitted contingency updates for the Winter and Light Load model. See ‘Rockport_revert_WIN_LL.con’ for contingency correction.